1. General.

In Operations Subdivision No 1 LK-1 gas compressor house it is planned to install Bently Nevada (BN) monitoring, protection and diagnostic system for compressors SK-301 and SK-302. For compressor condition monitoring and protection, respective hardware and software updates are required.

Compressor was manufactured by company 'Сумское МНПО им. Фрунзе'; type 2GM16-20/42-60CM2; 2-cylinder compressor designed to compress hydrogen gas mixture. Suction pressure – 32 bar, discharge pressure – 50 bar.

Electric motor type – СДКП2-18-26-16У4, power – 800kW, revolutions – 375 rpm.

Hardware and protection systems must be certified in accordance with ATEX Directive 94/9/EC – designed for use in explosive atmospheres. Compressors are operating in ex zone 1 (Attachment B).

2. Attachments.

Attachment A – sketch of compressor.

Attachment B – preliminary automation task.

Attachment C – plan of potentially explosive atmospheres at LK-1 Gas Compressor House.

3. Scope of Work and Work Specifics.

3.1. General requirements.

All works must be performed in strict compliance with the regulations of ORLEN Lietuva and of the Republic of Lithuania, as well as applicable specifications, drawings, recommendations of manufacturers, and other documents.

Prior to submitting a proposal, IT IS REQUIRED to visit the refinery and the facilities where the equipment will be installed, for the Contractor to better understand the scope of work and submit an accurate proposal.

3.2. Work description.

- Develop project execution schedule.

- Prepare detailed electrical, automation, mechanical part designs for the installation of monitoring, protection and diagnostic system for compressors SK-301 and SK-302 based on work description.

- The system must cover the following measurements:

- crosshead vibrations (2 measurement points per compressor);

- frame vibrations (2 measurement point per compressor);

- rod displacement (4 measurement points per compressor);

- revolutions (1 measurement point per compressor).

- New hardware cabinet in DCS room of Central Control Room of LK-1 will be required. Cabinet must be ordered, procured and installed by the contractor. Type and location of cabinet must be agreed with OL. Hardware installed in the cabinet must meet applicable OL fire safety requirements.

- System must be connected to the existing DCS for data transmission to operators via MODBUS.

- Alarms must be connected to the existing DCS system, interlocks to the existing relay interlock diagram. Interlocks must be based on redundant relay modules with separate shutdown signal outputs eliminating the possibility of shutdown due to the failure in the protection system. One shutdown signal from one relay module for each compressor must be designed. Alarm signals must be configured in DCS according to the provided automation task.

- All works, licenses and materials required for the connection of the system to the relay system for compressor shutdown and to DCS for operator interface must be included. DCS programming works shall be performed by OL.

- Configure sensor data transfer to existing System 1 server. Procurement, installation and configuration of all software and licensesare  within the SOW of the seller.

- All works and materials for the connection of the system to System1 EVO server must be included.

- New monitoring, protection and diagnostic system should be powered from UPS (to be agreed with OL).

- Two power supply modules must be installed in each rack. They shall be powered from separate uninterrupted power supply sources, eliminating loss of voltage possibility due to electric equipment failure or servicing works.

- The contractor must provide and coordinate with OL detailed drawings for the installation of the system (communication networks, auxiliary piping for cabinets and sensors, cable routing, 24 V DC and 230 V AC power supply diagrams, etc.).

- Update and submit new diagrams/tables of alarms/ESD.

- All existing electricity and automation single-line diagrams must be updated if any modifications were made in execution of this project.

- Order and deliver required equipment, materials according to the developed design.

- Prepare cable route according to the developed design, install new cable trays, if required.

- In local control panels of compressor SK-301 and SK-302, in each separately, design and install one joint yellow light indicator 'Activation of Bently Nevada alarm' and one joint red light indicator 'Activation of Bently Nevada interlock'.

- According to project execution schedule, upon agreement with OL, fabricate sensor holders and prepare points to attach them. In design documentation, provide detailed drawings according to which the holders were fabricated.

- Prepare measuring point on compressor or electric motor shaft for key phasor sensor following BN system requirements.

- Install new sensor, power supply and communication cables, their commutation equipment.

- Install new hardware cabinet in DCS room in pre-agreed place. Install system hardware in the cabinet.

- Perform new diagnostic system configuration and testing works in accordance with design requirements and present reports.

- In separate data carriers along with the design, present all software configuration documents and other information required to restore design settings of the software.

- Perform zero phase loop checks for the installed cables, check signals in the installed communication cables as required by IEC 62382. Present measurement documentation.

- Connect the system to the existing DCS system (MODBUS). Data must be accessible to operators. Relay interlocking output signals of the new system must be configured and connected to the relay system. Alarm signals must be configured in DCS.

- Perform commissioning/startup works.

- Include training of OL staff (2 people) on diagnostics of reciprocating compressors.

- Conduct training for the technological staff on the meaning and importance of the newly installed parameters.

- Prepare and submit AS-BUILT documentation.

3.3. Requirements for work execution and documentation.

- Project execution schedule must be developed and agreed with the Owner as the shutdown of the compressor for maintenance has to be agreed with the process staff.

- Contractor is required to order and provide sensors, monitoring system hardware and software required to monitor the condition of compressor and its motor as well as all commutation equipment needed to interconnect the installations.

- Sensors must be metrologically verified.

- Sensors shall be provided together with technical requirements and recommendations for their periodic inspections.

- Discrete output signals of the system must be connected to DCS.

- Hardware may be installed in the existing DCS room, using the ~270 meter cable route leading away from the compressor.

- According to automation task agreed with process engineers, the operator display (S-300 station) must provide the main real-time information which is required for operative control of equipment. Imaging is also necessary for operators in the machine room.

- Monitoring and diagnostics system electrical, automation and mechanical part design including technical conditions and all materials (including all required sensors, power supply and communication cables, their commutation equipment) must be provided.

- Contractor is required to inspect the quality of installation works, commission and transfer the system to the Owner together with reporting documentation required by OL.

- During the commissioning of the system, the staff of the Company must be trained on the general operational aspects, servicing and diagnostics capabilities of the system, as well as the key diagnostics principles.

- It is required to present all technical documentation of the system and its elements.

- As an option, provide a list of recommended spare parts for the implemented system.

3.4. Qualification requirements to Contractor.

Contractor must provide warranty for all works performed by it and installed materials. Warranty terms for both equipment and works must be provided.

Contractor must hold all licenses, certificates, etc. required for and related to the work and authorizing to perform works indicated in the SOW.

Contractor shall be responsible for all activities affecting the quality of equipment, materials and works.

4. Materials, equipment and services supplied by the Owner.

In its proposal contractor shall present and agree (get the Owner's approval) a request for materials, equipment and services to be furnished by the Owner.

The customer takes care of the scaffolding.

5. Materials, equipment and services provided by Contractor.

Contractor shall furnish the materials, equipment and tools necessary for the execution of works.

All materials, software, hardware and licenses shall be provided by the contractor

6. Requirements for completion of works.

The works must be completed by 31 December 2026.

7. Work transfer requirements.

Works and documentation must be verified and agreed with the Owner.

8. Requirements for work schedule.

The Contractor shall include its proposal with a detailed work execution schedule.