1. General.

[General description, purpose and place of works]

- Operations Subdivision No 3 (OS-3) Sulphur Production Unit (SPU) control system reliability improvement works include replacement of Sulphur Production Units, Reagent Section, Central Condensate Station (CCS), Sulphur Degassing and Granulation Unit (SDGU) Foxboro control system components and software changes. The works are to ensure proper and reliable operation of the control system for 6 years following the 2027 Spring Turnaround.

2. Attachments.

[List all related additional material (reference number and exact title of document). If any pictures, drawings or diagrams are provided to describe/illustrate the requirements, make sure that they are consistent with the requirements indicated in SOW].

1. Sulphur_25FEB2025_135857.ferx

3. Description and specifics of work.

3.1. Work description.

[Define and explain each work that needs to be done. Indicate the main steps and actions to be executed by Contractor. Specify preliminary sequence of works. When planning the scope of work, it is necessary to evaluate the results of inspections performed for the facility / equipment, to take into account the data of continuous inspections and previously recorded incidents (if any).]

3.1.1. Replacement of outdated operator, OPC and engineering workstations with new ones. The software versions shall be the latest available. The number of workstations to be replaced - 10 pcs.

3.1.2. Migration from ICC, IACC software to Control Editor.

3.1.3. Migration SMDH software to System Manager.

3.1.4. Migration AIM Historian to Historian.

3.1.5. FoxView/FoxDraw software upgrade to latest version. No upgrade to Control HMI is needed.

3.1.6. Perform all actual firmware upgrades for existing hardware.

3.2. Special requirements (if any).

[Indicate specific requirements which might impact performance of works, price, results. (E.g. recommend to visit the site at specified time, etc.)]

3.2.1. Any equipment installation and dismantling works shall be done by the Contractor.

3.2.2. Arrangements for returning of dismantled equipment shall be made, and the costs for such shall be borne by the Contractor.

3.2.3. Information stored on the media of being returned workstations shall be destructed before shipping out, or the media shall be handed over to the Owner.

3.2.4. The new workstations shall have SSD type media, RAID1.

3.3. Requirements for work execution and documentation.

[Specify the documentation to be provided by Contractor for work execution. If this is some data, indicate and describe the exact data needed and the standards to comply with. In case Contractor has to fill in some documentation, specify the desired format and contents, or refer to the requirements for the document preparation.]

3.3.1. The Contractor shall submit a preliminary work schedule.

3.3.2. All customs formalities should be done by Contractor.

3.4. Qualification requirements for the Contractor.

[Specify exact qualification requirements to be met by the Contractor. Describe requirements for works execution, design, reliability, staff, etc.]

3.4.1. The Contractor shall present qualification proving documents for Foxboro Control Software configuration and updating work.

4. Materials, equipment, and services to be provided by the Owner.

[If certain materials and equipment provided by Owner will be used by Contractor for specific tasks, indicate what exactly will be provided and when]

## None.

5. Materials, equipment, and services to be provided by the Contractor.

[List the items to be provided by Contractor as a part of works, and to be included in the price.]

## The Contractor shall supply all the other materials and equipment required for the works.

6. Requirements for work completion.

[Set the main milestones and deadlines or control points in the course of task execution where the Owner is to review the completed tasks, approve, accept such as proper, or reject them.]

6.1. Development of design;

6.2. Installation of equipment;

6.3. Programming and configuration works;

6.4. Demounting of no longer used equipment.

7. Requirements for work acceptance.

[Describe criteria according to which completed work will deemed compliant with requirements and accepted.]

The work shall be considered completed after functioning of the replaced system parts has been tested following AB ORLEN Lietuva procedures for FAT, SAT, SIT, also after licenses and configuration file copies have been presented.

8. Requirements for work schedule.

[Indicate preliminary work execution period. If period is indicated from the contract signature, such shall be given in calendar days, weeks or months.]

8.1. Development of method statement and agreement thereof with AB ORLEN Lietuva – before 30 January 2027.

8.2. Installation, programming, configuration and testing works on site (in the territory of AB ORLEN Lietuva) – from 26 April 2027 to 10 June 2027 preliminarily (exact time will be given later).

8.3. Demounting and shipping out of no longer used equipment – before 30 June 2027.