1. General.

- Installation of uninterrupted power supply sources (hereinafter, UPS) UPS-1 and UPS-2, and the electrical network for connected electrical equipment in the control room of the Chemical Water Treatment Unit (hereinafter, WTU) of Power House, according to the Design OLP02738 prepared by the OWNER.

2. Attachments.

Attachment No 1_Project OLP03738

Attachment No 2_Structural diagram

Attachment No 3_Air conditioner test report form

3. Description and specifics of work.

3.1. Description of work.

It is necessary to install new UPS (2 pcs.) with air conditioners on battery cabinets to supply power to devices connected to computer network in the control room of the Power House WTU. To power the UPS, the CONTRACTOR shall upgrade commutation equipment of existing 0,4kV cubicles, install new power cabinets 19JR431, 12JR433, cable routes and cables. To power the computer network in the control room of WTU, new computer network cabinets KS-1, KS-2, computer sockets, cable routes and cables shall be installed.    The scope of work is detailed in the Design OLP03738 prepared by the OWNER. After installing the new equipment, unused electrical installation shall be dismantled, necessary startup/commissioning activities and tests/measurements shall be performed in accordance with the applicable regulations.

3.2. Special requirements (if any).

- Partial payments, at the CONTRACTOR’S request, shall be made only if the CONTRACTOR has specified the milestones subject to payment (e.g., design, installation, startup/commissioning) in the proposal and submitted a corresponding payment schedule.

- To accurately assess the scope of work, the CONTRACTOR shall visit the site prior to submitting the proposal.

- As part of proposal, the CONTRACTOR shall submit preliminary quantity of scaffolding and the duration of use to complete the works indicated in this SOW. Placement of the scaffolding shall be planned only where mobile lifting equipment (cherry pickers, lifts, etc.) cannot be used.

- Supplied UPS units must include pre-entered commissioning codes if the CONTRACTOR is competent to perform commissioning independently. In other case, the CONTRACTOR’S proposal shall specify that the startup/commissioning activities of UPS shall be performed by the provider of the UPS or the SUBCONTRACTOR.

- The maintenance alarm of the UPS shall be turned off/deactivated.

- Works in electrical installations shall be performed according to work permits for electrical works.

3.3. Requirements for work execution and documentation.

## 1. CONTRACTOR shall perform all works specified in the design, also the works arising during the installation activities that are needed to ensure safe and proper operating conditions.

## 2. During installation of new cabinets, internal wiring, and cable trays, provision shall be made for future connection of equipment feeding lines from these cabinets under other projects. The number of spare terminals and sealing devices shall be at least equal to the number of spare circuit breakers.

## 3. Proper startup/commissioning activities, measurements and tests, specified in the Norms and Scope of Electrical Equipment Testing, shall be performed. Test reports and other technical documentation shall be provided.

4. Accumulator battery capacity and other measurements shall be performed after finishing installation works in the power substation, during the startup/commissioning activities.

5. The CONTRACTOR shall mark the UPS air conditioners in accordance with the applicable legislation. The conditioner codes (KO-xxx) shall be provided by the Engineer of Critical Equipment Maintenance Group responsible for the maintenance of conditioners. After the air conditioner installation works and startup/commissioning activities, the CONTRACTOR shall fill in the test report form of air conditioner provided in Attachment No 3.

6.  The installation of the UPS air conditioner condensate drainage shall be discussed and agreed with the OWNER when assessing the scope of work. Discharge of condensate on the floor of the switchgear or elsewhere is prohibited.

7. Upon completion of installation works, the CONTRACTOR shall provide documentation detailing any changes made to the original design solutions along with corresponding AS BUILT designs.

8. The CONTRACTOR shall deliver all dismantled equipment to a location designated by the OWNER within OL territory.

9. The CONTRACTOR shall seal all floor openings resulting from the dismantling activities, restore the affected floor surfaces.

3.4. Qualification requirements for Contractor.

1. CONTRACTOR and/or its SUBCONTRACTORS must have certificates issued by the State Energy Inspectorate of the Republic of Lithuania for:

1.1. Operation of power network and facilities with voltage up to 1000 V;

1.2. Testing of power network and facilities of up to 1000 V;

2. All permits required for works (e.g., permits for electrical facilities, hot works) shall be obtained by the CONTRACTOR in accordance with OL procedures.

3. For the evaluation of the technical part of the proposal the CONTRACTOR shall submit the following:

3.1. An analysis of the current situation, accompanied by a detailed description of the works;

3.2. A work execution schedule aligned with the payment schedule;

3.3. Lists of works of similar scope completed within the past five years. If the CONTRACTOR is performing startup/commissioning activities of UPS, the list of works shall also include this type of works;

3.4. A list of subcontractors.

4. Materials, equipment, and services provided by OWNER.

OWNER shall provide scaffolding.

5. Materials, equipment, and services provided by Contractor.

## 1. CONTRACTOR shall provide all materials required for the implementation of the project.

## 2. Technical descriptions (manuals) of equipment in Lithuanian shall be submitted to engineering staff together with the equipment.

3. CONTRACTOR shall prepare and approve with the OWNER an operating instruction of UPS for the operational staff in accordance with the OWNER’S document preparation requirements. This instruction is in accordance with the scope specified in Paragraph 48 of Rules for Operation of Power Plants and Power Networks.

4. CONTRACTOR shall provide equipment, work tools, lifting mechanisms and special equipment necessary for execution of the works.

6. Requirements for work completion.

1. Installation of equipment.

2. Commissioning/startup.

3. Agreeing with the OWNER on operation instructions of UPS for operational staff.

4. Demounting of equipment that is no longer used.

7. Requirements for work acceptance.

The works shall be deemed fully completed after the Certificate on Electrical Equipment Fitness for Service has been issued in accordance with AB ORLEN Lietuva procedures, and the drawbacks specified in the certificate have been eliminated. Documents submitted by the Contractor shall include:

- USB with AS BUILT design drawings in DWG format;

- USB with AS BUILT design drawings in PDF format. Each document listed in the project documentation and drawing registration shall be submitted as an individual file. File names must exactly match the document designation and include the corresponding revision number.

8. Requirements for work schedule.

Preliminary Work Schedule:

- Installation works – by 30 September 2026.

- Startup/commissioning activities – by 31 October 2026.

- Submission of technical documentation, receipt of Certificate on Fitness of Electrical Equipment for Service.