| AB ORLEN Lietuva Electrical and Automation Department Technical Inspection and Analysis Group |  |  |  |
| --- | --- | --- | --- |
| 930-00. OS-3 Flare Section Reconstruction SCOPE OF AND REQUIREMENTS FOR DESIGNING Rev. 1 |  |  |  |
| 2025-10-09 Juodeikiai Village, Mažeikiai Distr. |  |  |  |
| FACILITY: | 930-00, OSBL COMMUNICATIONS AND FLARE SECTION |  |  |
| OWNER: | AB ORLEN Lietuva (hereinafter – OL or the Owner) |  |  |
| DESIGN NUMBER (design documentation ID): | OLP02729 |  |  |
| TITLE: | 930-00. OS-3 Flare Section Reconstruction |  |  |
| DESIGN PART: | Process Control and Automation (PCA) |  |  |
| DESIGN PHASE: | Detailed engineering design (hereinafter, DD) |  |  |
| DESIGNER: | Designing company, its representative (hereinafter – Contractor or Designer) |  |  |

# OBJECTIVE

  - Developing the process control and automation design based on the detailed Scope of Work (SOW) provided herein, together with the attached Automation Design Task (ADT) and other referenced documents.

  - This Design shall focus on automation and process control, while other disciplines shall be addressed only to the extent required for the preparation and physical implementation of this Design.

# BASIC REQUIREMENTS FOR DESIGN

## The detailed engineering design (DD) shall conform to the laws of the Republic of Lithuania and European Union, Technical Regulations for Construction (STR), Rules for Installation of Electrical Equipment, as well as other documents effective in the Republic of Lithuania to be followed in preparing DD, also the requirements set forth herein and in the equipment manufacturers’ manuals.

## The designed equipment shall be suitable for the site ambient conditions.  The equipment, structural steel and cabling systems shall be suitable for use in C3 or C4 corrosion environment. Minimum required zinc coating on hot-dip galvanized structures is 60µm at least. If an alternative corrosion protection method is applied, it shall provide a level of protection equivalent to hot-dip galvanization, ensuring a minimum service life of 20 years. The minimum wall thickness of wiring ducts shall be 1.5 mm.

## The newly designed equipment and materials shall be selected according to OL requirements. The designed equipment shall be selected considering the type of explosive zone, category of explosive mixture and temperature class.

## Instruments designed in explosive atmospheres shall have ATEX conformity certification, as used in the European Union. Potentially explosive zones shall be indicted on the equipment layout drawings.

## Control cables for instrumentation loops shall be selected according to OL requirements.

## All the designed electrical equipment shall be marked (tagged) according to OL requirements for marking of electrical equipment.

## All materials specified in the design shall meet the requirements of applicable legislation and have certificates valid in the Republic of Lithuania.

## The designer shall take care of all mandatory documents, tests and/or measurements required for the design.

## The existing grounding system shall be used for the designed equipment with new grounding equipment designed where necessary.

## The design shall provide for proper protection devices for electric users, their data and safety circuit calculations.

## Measuring instruments and equipment shall be installed in such a way that they and their components can be easily maintained, cleaned, repaired and inspected without using any auxiliary devices (scaffolds, ladders, etc.).

## All engineering solutions, designed equipment and materials shall be coordinated with OL   Electrical & Automation Department’s Technical Inspection & Analysis Group, Automation and Power Engineer supervising the respective process facility,  Process Control Systems Development Group Engineer, and IT Department Engineer.

## If, in the course of designing, the need for any additional equipment arises, such shall be approved by the Owner.

## The Design shall include the dismantling of obsolete components and define the scope of dismantling work to be performed.

## The Designer shall visit the facility to verify the technical parameters of existing equipment, the installation place, etc. specified in OL documents, and only after making sure that such information is correct use it in design solutions.

## The Designer shall submit all relevant technical documentation (equipment layout plans, installation/functional diagrams, schematics for connection and wiring, basic measurement diagrams (loop drawings), diagrams for selection and hook-up of new instruments and equipment, 24 V DC power supply diagrams, drawings of cable routes, cable markings (tags), explanatory note, etc.) according to OL requirements.

## The Designer shall coordinate any design solutions that may affect existing civil structures with the Civil Construction Technical Supervision and Maintenance Manager.

## Where this Design affects electrical, process piping, construction, communication and other design disciplines, it shall be coordinated with the developers of those disciplines to ensure compatibility of solutions.

## The title block of each drawing shall display the facility identification number (facility number) and the Owner’s design document identification number (design document ID).

## DD documentation/drawings shall be provided by the Designer in the Lithuanian (national) language. The Contractor’s package of drawings shall include all the drawings required for work execution. In case the Contractor is a foreign company, DD documents (title page, explanatory note, comments, and explanations on design drawings) shall be made in Lithuanian, other design documents may be in English.

## DD – drawings, diagrams, specifications, logbooks, etc. shall be presented to the Owner for review and comments in a digital form (PDF, DWG format). For the final coordination of DD, the original DD signed by the Designer and Design Work Manager shall be provided as hard copy and in digital form (PDF and DWG format) by e-mail or in case of large amount of documents by using link ‘https://nextfile.orlen.pl’; text documents, if any, shall be in MS Word DOC format, MS Excel XLS format. The original copy of DD shall have 'APPROVED’ mark by OL.

## Once completed, DD shall be agreed with OL specialists indicated by the Project Manager.

## Once approved, DD shall be handed over to the Owner as required under OL procedures. Documentation shall be prepared for transfer to OL archive in accordance with OL archiving requirements.

# GENERAL SCOPE OF DESIGNING

## Developing the detailed engineering design OLP02729 for the process control and automation (PCA) discipline. The main input data and scope for this detailed engineering design are provided in the design proposal package for OLPP225 ‘930-00, Replacement of OS-3 Flare Stacks D-2 and D-4’. This package includes P&IDs, the explanatory note for the process discipline, the design task for the PCA discipline (hereinafter – ADT), flare datasheets, and other related documents.

## The primary objective of this design is to replace the existing D-2 flare stack with a new unit of greater capacity and height. In addition, a new D-4 flare with increased capacity will be designed in accordance with the requirements of the FLUOR study. Both flares, D-2 and D-4, will be designed to ensure that, in the event of an emergency, each can serve as a backup for the other.

## According to P&ID FU-26-D2: The number of instruments for the D-2 flare will be determined after the proposal is received. During the detailed design stage, it will be assessed whether the steam supply system for smokeless combustion requires modifications, including redesign of the existing flow meters, valves, and the piping from the header to the flare to accommodate a larger nominal diameter (DN). Design a smokeless visual control system when mounted on the ground the sensor monitors the flame of the main flare and automatically opens and adjusts steam feed valve.

## According to P&ID FU-28-D4: The number of instruments for the D-4 flare will be determined after the proposal is received. During the detailed design stage, it will be assessed whether the steam supply system for smokeless combustion requires modifications, including redesign of the existing flow meters, valves, and the piping from the header to the flare to accommodate a larger nominal diameter (DN). Design a smokeless visual control system when mounted on the ground the sensor monitors the flame of the main flare and automatically opens and adjusts steam feed valve.

- Design piping heating operation status indication to DCS screens inside flare farm control room

## During design execution, once the final number of new instrument positions has been confirmed, the corresponding tag numbers shall be obtained from the Owner. All datasheets, design documents, and other deliverables for the new instruments shall be prepared using the tag numbers provided by the Owner.

## HAZOP/SIL risk assessment

### If, within the overall design scope, a HAZOP/SIL study is conducted and a protection level of not less than SIL-1 is assigned, SIL verification calculations shall be performed. Any design modifications or additions required to achieve the specified SIL level shall be incorporated into the design.

### The Contractor shall submit to the Owner a SIL assessment report together with the associated verification calculations. It is preferred that the calculations be performed using exSILentia software, and that the corresponding exSILentia calculation file be provided.

### The interval between two full stroke tests (FST) shall not be less than six years. Additional required data are specified in OL TR 12 Technical Requirements.

### The Contractor shall prepare a proof test procedure, define SRS requirements, and provide SIL certificates as well as safety manuals.

### Other HAZOP recommendations, if assigned to the PCA discipline, shall also be implemented.

## ATEX

### If, during the design stage, explosive atmospheres are modified or extended, the PCA discipline designer shall evaluate the suitability of the existing equipment for such atmospheres and, if necessary, redesign such equipment.

# DESIGN WORK SCOPE FOR INSTRUMENT SELECTION AND SIGNAL INTEGRATION

## For the preliminary quantities of new instruments and other information required for the development of the PCA discipline, refer to the enclosed process design package OLPP225. The exact quantities of new instruments shall be specified after the HAZOP/SIL risk assessments have been completed and the final detailed process design for the flare stacks, P&IDs, datasheets, and other related documents have been prepared.

## Refer to the OL Technical Requirements (Attachment 1) for the main requirements applicable to the selection and design of equipment. General requirements for different types of instruments (if any are designed under this document), as well as potential design solutions for signal integration, are provided below.

## Temperature measuring instruments (TE/TT-***)

### Selecting and designing the connections for new temperature measurement points using flanged thermowells for process piping and vessels. Providing thermowell strength calculations in accordance with ASME PTC 19.3 requirements. Specifying the types and installation of other temperature sensors in accordance with the ignition and control system manufacturer’s requirements.

### Designing separately installed HART temperature transmitters with 4–20 mA Exia output signals for positions used in control and interlock loops.

### Designing new GM multiplexers with cabinets (for the installation of at least two modules) for connecting the remaining positions to the ACS. Re-checking the number of cabinets, cabinet sizes, and their layout within the unit during the design phase, considering the available space and reserve capacity.

### Verifying onsite during the design phase the possibility of utilizing existing spare multiplexer channels for signal integration.

## Pressure measuring devices (PT-***)

### Designing new electronic pressure transmitters and their wiring in an O‘BRIEN-type instrumentation cabinet, equipped with electric heating and local disconnection of the heating power supply. Designing an electric radiator equipped with a thermostat for heating the instrument cabinet. Power supply for electric heating is provided in the electrical design.

### Designing process connections using heated impulse lines and Swagelok fittings. Designing end couplings of impulse lines with visual (light) indication.

### Designing transmitter standard measuring signals as 4–20 mA HART, two-wire, 24 V DC, powered from the loop. Applying ATEX Exia design to instruments.

## Level transmitters (LT-***)

### Selecting and designing the hookup of level transmitters and integration of their signals into the automated control system (ACS).

### The provisional location for mounting the level transmitters (flange-type, radar, and microwave) is inside the level columns, with the final location to be confirmed after preparation of mechanical drawings.

### Providing transmitters with a standard measuring signal of 4–20 mA HART, two-wire, 24 V DC, powered from the loop.

### Applying ATEX Exia design to the instruments.

## Control valves (PV, FV-***)

### Designing the hookup of control valves with electro-pneumatic positioners and signal integration into the DCS.

### Designing the air supply using Swagelok connectors and tubing. Designing valves for connection to the air supply, where required.

### Equipping all valves with an air filter/reducer and an Exia electro-pneumatic positioner.  Designing control signal as 4–20 mA, HART protocol, two-wire, powered from the 24 V DC loop.

## Motor operated valves (ESK)

### Designing the integration of signals from motor-operated valves (MOVs) equipped with Rotork electric actuators into the ACS. Defining the main actuator control signals as: ‘Close’, ‘Open’ and the status signals as: ‘Closed’, ‘Open’, ‘Local/Remote’, ‘Fault’. All signals shall be 24 VDC.

### Providing control discrete signals for all fail-open or fail-close valves, with separate cable connections to the ESD system or control panel.

### Power supply to electric motors will be covered under the electrical discipline.

## D-2 and D-4 ignition and control equipment

### Selecting and designing flare ignition and control equipment, including wiring to field cabinets, control stations, and junction boxes. Connecting temperature, flame control, alarm, and control signals as required for the ordered equipment.

### Designing the integration of signals into the Flare Section ACS.

### Designing the power supply for flare ignition and control equipment from the UPS system. Power supply connection will be covered under the electrical discipline.

## Junction boxes, cables, cable routes

### Designing new junction boxes and mains for the transmission of signals to the ACS.

### Evaluating onsite the possibility of using existing junction boxes and spare cables for the connection of new signals, in coordination with the Unit’s Automation Engineer and taking into account the distribution of this equipment within the Unit.

### Designing new protective conduits (steel, galvanized) and cable routes where required. Designing supporting structures where required. Verifying details and other requirements onsite.

## Signals to MCC (electrical substation), if any required

### Designing connections for DI/DO and AI/AO signals from the substation to the ACS via marshalling cabinets.  Marshalling cabinets will be covered under the electrical discipline.

### Marshalling cabinets will be equipped with auxiliary relays (230VAC/24VDC and 24VDC/230VAC), converters, terminal blocks and other required equipment.

### Design in E part planned piping heating operation status indication to DCS screens inside flare farm control room;

### Design in E part planned uninterruptible power supply units operation status indication to DCS system;

### Ensuring all signals between the MCC and the DCS are 24 V DC.

## DCS/ESD

### Integrating the newly designed control and status signals into the Flare Section Siemens ACS, which is used for monitoring and operating the technological process as well as for process interlocks. Integrating the interlocking signals into the ESD modules using separate cables.  Connecting instrumentation readings, alarms, and control signals to the Flare Section control system workstations and the PI server.

### The Contractor shall apply, during the design phase, to OL Control Systems Group engineers to obtain/coordinate information on the addresses for new signal connections to the existing spare modules, and to identify the need for additional I/O modules.

### The Contractor shall note that OL has initiated implementation of design OLP02715 for upgrading the Siemens PLC control system by replacing the existing system (Siemens S400HF PLC with I/O, IM, CM, PS modules) with the new Siemens S-400HF or S-1500HF series, and by replacing redundant PLC and I/O, CM, IM modules with ET200MP or ET200SP HA type modules.

### In addition, design works under OLP01443 JI2048 PETROFAC New RHCU Flare ‘460-00 Įr-4, S-1000 – Residue Hydrocracking Unit Construction’ are currently in progress, and the existing I/O channels have been reserved in advance.

### The control system block diagram for the Flare Section control room and the I/O list for the existing controller are provided in Attachment 7.

### The existing design drawings are provided in Attachment 8.  It should be noted that, throughout the ongoing service period of the Flare Section, various designs have been developed and implemented at different times, supplementing the original design on which the current Siemens PLC control system was installed.

ATTACHMENTS:

- OL technical requirements from Electrical and Automation Department.

- OL electrical equipment tagging (abbreviations).

- Requirements for control cables.

## Handover of DD.

- Design registration card.

- OLPP225 process design proposal

- The existing ACS architecture, list of IO.

- The existing PCA designs.

- FS hazardous (Ex) area zoning plan.

- List of manufacturers.

PREPARED BY:

Technical Inspection and Analysis Group 		Rimantas Bagdonas

Engineer Expert

AGREED WITH:

Technical Inspection and Analysis Manager 	                       Evaldas Lungys