ORLEN LIETUVA JOINT STOCK COMPANY

ELECTRICAL AND AUTOMATION DEPARTMENT

DESIGN TASK

FOR PROJECT "672-10. SGĮ-, 1 increase conversion to 98.5%. Capital repair"

(rev.2)

ELECTRICAL ENGINEERING PART

2026-01-16

Juodeikiai, Mažeikiai district

OBJECT: 672-10 Sulfur production unit No. 1 with MEA regeneration block

CUSTOMER: ORLEN Lietuva Joint Stock Company

CUSTOMER PROJECT NO.: OLP02233

PROJECT PART: electrical engineering

PROJECT STAGE: Combined Technical & Working Design (Detailed Technical Design) (TWD)

DESIGNER: design company, its representatives.

# BASIC REQUIREMENTS:

  - The project must comply with the Electrical Equipment Installation Rules (EĮĮT), Lithuanian regulatory documents, Construction Technical Regulations (STR) and the client's requirements.

  - The design must include engineering studies (assessment of existing equipment, analysis and verification of diagrams and documentation, and other actions necessary for assessing the current situation and making design decisions), the electrical engineering part of the designed object, including the grounding of related facilities and equipment, protection against lightning and overvoltage, and other parts of the project necessary for the proper installation and use of the object.

  - The designed equipment shall be according to the environmental conditions of the installation site. Cable and metal structures shall be suitable for use in a C3 or C4 corrosion class environment. The zinc thickness of hot-dip galvanized structures shall be not less than 60 µm. When using other methods of corrosion protection for metal structures, the level of protection must be no lower than that of hot-dip galvanizing and remain corrosion-resistant for >20 years. The thickness of cable trays must be no less than 1.5 mm.

  - Switching devices (automatic switches, connectors, disconnectors, isolators, earthing switches, equipment control devices, etc.) that connect voltage to circuits must have padlocking points, which are usually provided by the manufacturer and are intended for locking in the disconnected position (LoTo function).

  - The title number of the object and the customer's project number shall be indicated in the main title block of the drawings.

  - The language of the project documents (title page, explanatory note, comments and explanations in the project drawings)- Lithuanian. English may be used in other parts.

  - When preparing the project, the designer must follow the specifications and description of the scope of work provided by the client. However, the designer is responsible for the correctness of the design solutions and their compliance with regulatory acts. The client will provide methodological assistance in obtaining the existing documentation and regarding the use of existing elements.

  - The CLIENT may provide paper or scanned copies of initial and subsequent designs, operational diagrams related to the work being performed, in Lithuanian or Russian. The designer must visit the site, check the information provided in the documents submitted by the CUSTOMER regarding the technical parameters, installation location, and dimensions of the existing equipment, and, after verifying their accuracy, make design decisions.

  - The electrical equipment to be designed must be selected after assessing the type of explosive zone, the category of explosive mixture, and the temperature class. The project drawings, which show the plans with the equipment designed for explosive environments, must indicate the classification of the explosive environment zone, the category of the explosive mixture, and the temperature class.

  - The designed equipment must ensure efficient use of electrical energy, be safe and easy to operate.

  - The designed electrical distribution equipment and networks must be designed with a reserve of at least 30% of power and 20% of additional connection capacity.

  - The designer must be authorized to perform work on operating electrical installations up to 1 kV and above 1 kV (for the assessment of diagrams and substation equipment).

  - The project must select appropriate electrical receiver protection devices, calculate and specify the protection settings.

  - The project must include calculations of short-circuit currents, minimum single-phase short-circuit currents, voltage losses, and ensure the selective operation of existing and designed protective devices.

  - The project must provide for the dismantling of obsolete circuit elements (relays, cables) and equipment, and specify the scope of work for dismantling the equipment.

  - If a new receiver is connected or an existing receiver is replaced when designing an existing switchboard, power control panel, distribution or power supply panel, an updated single-line diagram of the entire panel must be prepared, showing the existing and designed receivers. When preparing the diagram, the operational and preliminary design diagrams must be used, and the designer must verify the accuracy of the information provided therein during equipment inspections. If it is necessary to measure voltage, current, or power, a request must be submitted to the customer's work supervisor to organize the necessary measurements.

  - The minimum set of documents for the project and the structure of document marking are specified in Appendix No. 4.1. The project may also include other additional documents explaining the design solutions.

  - Graphical symbols in electrical diagrams must comply with the requirements of LST EN 60617.

  - Electric cable lines must be numbered according to the cable line coding system provided in Appendix No. 4.2.

  - Appendix No. 4.3 provides a list of receiver abbreviations for the design, modernization, and operational management of electrical equipment, which must be followed when preparing the project.

  - Appendix No. 4.4 provides a table of harmonized cable codes, which must be followed when preparing the project.

  - Lay cables in existing cable routes and design new cable routes where necessary. Power cables must not be laid in the same cable routes (trays, ladders) as cables for control and measurement devices or control systems.

  - When designing mechanical cable protection   with flexible protective sleeves, provide for metal or metal-plastic protective sleeves together with cable entry (sealing) connections specified by the same manufacturer.

  - If necessary, prepare drawings of the construction and structural part for the installation and fastening of cable routes, electrical distribution boards, cabinets, and service areas. The construction and structural part of the project must be prepared by a qualified designer in accordance with the task and instructions prepared by the electrical engineer , and the design solutions and project must be agreed with the relevant CUSTOMER specialists.

  - Existing grounding equipment shall be used for the grounding of the designed equipment. If it is not possible to use the existing grounding equipment or if it is unsuitable, new grounding equipment shall be provided.

  - All engineering solutions must be coordinated with the engineer of the Technical Control and Analysis Group of the Electrical and Automation Department of the client and the engineers of the maintenance and repair group of the relevant facility.

  - If the project solutions will have an impact on building structures, the solutions must be coordinated with the building maintenance and repair manager.

  - The customer shall provide (as necessary) additional information required for the analysis of diagrams and calculations about the existing electrical network in accordance with the list of necessary information provided by the designer. The list and deadline for the submission of information shall be agreed separately.

  - For CLIENT comments documents shall be provided with the main drawings, diagrams, specifications, and data sheets (at least 80% complete) in digital form (.pdf and .dwg). For final approval, hard copies signed by at least two different persons, shall be submitted: the DESIGNER (the employee who prepared the project and the project manager (PDV)) and the relevant manager of the DESIGNER's company who checked the documents. The project shall be coordinated with the CUSTOMER's employees specified in the "Project document and drawing coordination form". The CLIENT's Electrical and Automation Department Technical Control and Analysis Group engineer expert/senior engineer/engineer shall mark the project documents with the appropriate stamp when coordinating the project. The approved and signed project documents in editable digital form (.dwg, .doc, etc.) shall be sent separately by e-mail, larger files shall be sent via the https://nextfile.orlen.pl system,   to the employee of the Technical Control and Analysis Group who approved the project.

  - Newly designed equipment shall be designed in accordance with the CUSTOMER's general electrical requirements – technical specifications (in English) provided in Appendix No. 4.5. Select equipment from the list of manufacturers provided in Appendix No. 4.6 (in exceptional cases, other manufacturers may be considered in agreement with the CUSTOMER).

- Scope of design.

  - Replacement of the existing 6/0.4 kV 1000 KVA power transformers T-1, T-2 (2 units) in the TP-16 KTP substation with 1250 KVA power transformers.

  - Replacement of the existing 0.4 kV switchgear TP-16 JVS-1 and installation of a 0.4 kV distribution cabinet 16PS-1X   with an automatic power transfer switch (hereinafter referred to as AMP).

    - The existing structural power supply diagram of substation TP-16 is provided in Appendix No. 4.7

    - Since other solutions for   will be designed in the future under this project number and name, a separate project book or file No. 1 with the name "Increasing the power of transformers T1 and T2 at substation TP-16 and reconstructing the 0.4 kV switchgear JVS-1".

- DETAILED DESCRIPTION OF THE PROJECT SCOPE.

  - Replacement of existing 1000 kVA transformers T-1 and T-2 in the 6/0.4 kV TP-16 KTP distribution substation with 1250 kVA transformers.

    - The layout plan of TP-16 equipment is provided in Appendix No. 4.8

    - The existing single-line diagram of TP-16 KTP is provided in Appendix No. 4.9.

    - The technical data of the existing transformers is provided in Appendix No. 4.10.

    - An overview of the existing KTP switchgear with transformers is provided in Appendix No. 4.11.

    - The main technical data of the existing KTP substation is provided in Appendix No. 4.12.

    - Main technical requirements for new 1250 kVA transformers:

      - Type: Hermetic, oil-filled.

      - Power - 1250 kVA.

      - High voltage – 6000V AC.

      - Low voltage – 400V AC.

      - Frequency - 50 Hz.

      - Connection group -   Yyn0.

      - Short-circuit voltage Uk-5%

      - Voltage switching branches - 5 (6000V±2x2.5%).

      - Cooling ONAN (natural).

      - Protection rating – IP44.

      - Temperature control device with contacts – yes.

      - Pressure control device with contacts – yes.

      - Grounding terminals – yes.

    - Other general requirements for transformer installation are provided in the specification in Appendix 4.5   OL-TR-ER-013

    - The project includes drawings of the structural part (and the construction part, if necessary) for the transformer installation site, the widening of the oil pit, and the installation/replacement of transformer guides.

    - Prepare detailed drawings for connecting existing 6 kV cables to the new 6 kV inputs of the transformers.

    - Prepare detailed drawings for connecting 0.4 kV busbars between transformers and 0.4 kV switchgear (KTP) inputs to the switchgear.

    - Perform recalculations of the relay protection settings for TP-16 T1, T2 power supply, 6 kV cells PP-2 n.21, n.28 due to increased transformer power. Submit the relay protection settings. The existing relay protection settings for cells PP-2 n.21, n.28 are provided in Appendix No. 4.13.

    - Perform recalculations of the settings for the protection of the input and sectional automatic switches of the TP-16 0.4 kV switchgear (KTP) due to increased transformer power. Provide protection settings. The existing settings for the protection of the 0.4 kV KTP input and sectional automatic switches are provided in Appendix No. 4.14

    - The short-circuit current values on the busbars of sections 1 and 2 of the PP-2 6 kV switchgear are provided for the calculations: Ik3(max) – 14.2 kA; Ik3 (min)- 6.4 kA.

    - Provide for the connection of transformer temperature and pressure control devices to the existing control schemes.  The existing transformer temperature and pressure control scheme   is provided in Appendix  No. 4.19.

  - Replacement of the existing 0.4 kV switchgear TP-16 JVS-1.

    - The location of the existing JVS-1 is shown in Appendix No. 4.8.

    - The existing single-line diagram of JVS-1 is provided in Appendix No. 4.15.

    - For the power supply of the existing TP-16 JVS-1 (hereinafter JVS-1) electrical receivers and the connection of additional electrical receivers in the future, a new 0.4 kV switchgear JVS-1 and a 0.4 kV distribution cabinet 16PS-1X   with an automatic power switching diagram (hereinafter referred to as AMP) shall be installed in place of the existing switchgear JVS-1.

    - Install   in place of the existing switchboard JVS-1, after dismantling it.

    - The installation of 16PS-1X (the cabinet number will be specified during the preparation of the Detailed Technical Design) is planned in the TP-16 room.

    - The typical AMP diagram for 16PS-1X is provided in Appendix No. 4.18, for the basis of designing the AMP diagram. Note: 16PS-1X must have two cabinets, one of which must contain the AMP diagram elements, while the other must contain automatic switches for connecting receivers.

    - Appendix No. 4.16 provides a preliminary single-line diagram of the replaceable TP-16 JVS-1 switchboard and the new 16PS-1X. The diagram shows the main design parameters/ limits and the technical parameters of the automatic switches. The diagrams provided are based on the diagram for designing the new JVS-1 and 16PS-1X.

    - Appendix No. 4.20 presents preliminary internal diagrams of the cabinets, which were used as a basis for designing new cabinet diagrams. The diagrams indicate the minimum number of devices.

    - Plan to switch the existing JVS-1 electronic receivers to the newly designed JVS-1 and cabinet 16PS-1X.

    - Plan new cables for powering the JVS-1 inputs from TP-16 KTP cabinets 3-3 and 7-3.

    - For the protection of JVS-1 inputs, provide for the installation of new In-630A automatic switches in TP-16 KTP cabinets 3-3, 7-3. Prepare mechanical drawings for the installation of automatic switches on existing pull-out trolleys.

    - Appendix No. 4.17 shows the existing control diagrams for motors connected to JVS-1.

  - Basic requirements for replacing TP-16 JVS-1 and installing 16PS-1X:

    - JVS-1, Nominal current of busbar sections 1 and 2 - In-800A, 16PS-1X - In-100A Nominal operating/insulation voltage - 1000 V, 50 Hz, nominal impulse voltage - 8kV, nominal permissible short-circuit current (1 s) (thermal resistance 25kA).

    - JVS-1 automatic switches, power circuit breakers: 3-pole, molded case. Drawers - withdrawable type. Drawer form - 4b.

    - Automatic switches must be equipped with adjustable overload and short-circuit protection.

    - The protection blocks of automatic switches in motor supply cubicles must be designed for motor protection.

    - Ammeters L1, L2, L3 for measuring the currents of the busbars in the switchgear.

    - Voltmeter, voltmeter switch (L1-L2, L2-L3, L3-L1, L1-0, L2-0, L3-0 for controlling the voltage of the busbars and input cables).

    - Cabinet doors must have metal locks (double-bit lock inserts) with keys.

    - The locations for installing removable earthing switches must be provided and marked in the switchboard input and line power supply compartments, as well as in the section busbars.

    - The installation location of the sectional automatic switch   SA and sectional circuit breaker SK must ensure safe repair of sections 1 or 2 (without power from the non-repairable section).

    - The inscriptions and technical numbers on the equipment must be in Lithuanian and agreed with the CUSTOMER. The inscriptions must be on plastic plates, replaceable in frames or screwed on with screws, with a font size >10 mm. The names of the power supply lines must be on the front and rear doors of the cabinet.

    - The numbering of the cages consists of the cabinet number and the cage serial number. (e.g., Cabinet No. 3, Cage No. 1, marked n.3-1). The numbering of the cages must be on the front and rear doors of the cage. (Cage numbers must be agreed with the customer prior to the manufacture of the switchboard).

    - All secondary circuit terminals must be numbered and selected to match the cross-section of the conductor being connected. The conductor connection is screw-type. Only one wire may be connected to each terminal.

    - Control and measurement circuit wires must be numbered and marked at both ends. The wire marker must indicate the connection address of the wire (terminal and terminal) and the connection address of the other end of the wire (e.g. X1-2>KL1-14,   KL1-14>X1-2).

    - The internal wiring of the switchboard must be in PVC installation ducts, pipes, 	protected with protective tape. Wires must not be attached directly to the switchboard structures.

    - Use automatic switches (not fuses) to protect secondary circuits.

    - Other general requirements for switchboard installation are provided in Appendix No. 4.5 of the technical specification OL-TR-ER-005.

  - General requirements for the modification/reconstruction of TP-16 JVS-1.

    - When preparing a project for the dismantling of the existing switchgear and the installation of a new one, it is necessary to take into account that the replacement of switchgear is only possible during the Turnaround. (Preliminary - 18 days, duration to be agreed separately with the customer).

    - The project must specify the stages of the replacement of the   switchgear.

    - The equipment, panels, and cabinets located in the substation premises may be moved to another location, subject to agreement with the customer.

    - Existing power and control cables inside the substation building must be replaced with new ones.

    - The existing cables for remote control, self-contained circuits, and motor control circuits (to/from DCS ESD) shall remain in place. If the length of the existing cable   is insufficient for switching to the new switchboard, TP-16 shall install intermediate connection cabinets (hereinafter referred to as TSS) with connectors for cable connection/extension.

    - It is prohibited to install couplings in the substation cable ducts for the extension of existing power cables. Couplings must be installed outside the substation, in places accessible for visual inspection.

    - All cables (newly designed, switched, dismantled) must be entered in the cable log. The diagrams of switched, newly installed, dismantled cables (power, control cables) must indicate the terminals for connecting/switching/disconnecting both ends of the cables.

    - Provide for the renewal of existing power and control cable markings at both ends of the cable. Power and control cables must be laid in separate cable routes. 230 V AC   , and 24 V DC control cables must also be laid in separate cable routes.

    - Cables for electrical equipment that back each other up must be laid in separate cable routes, maintaining a distance of >600 mm from each other. In exceptional cases (if technically impossible otherwise), cables for redundant electrical equipment may be laid in separate compartments of trays and shelves with continuous A1 fire rating partitions with a fire resistance rating of at least EI 15.

  - Other requirements.

  - The designer must also implement works and measures not specified in the scope of work of the customer, which are necessary for the successful achievement of the project objectives and depend on the specifics of the equipment offered by the contractor, which are unknown to the customer when preparing these scopes and requirements and are therefore not specified.

  - The project specifies that the Contractor must build, assemble, install, perform commissioning and adjustment works for the designed equipment, and prepare as-built and operational documentation. Prepare the facility for operation and approval for use, hand over the facility to the customer and the controlling or relevant permit/certificate issuing authorities.

  - When submitting proposals for design work (technical assessment), the following must be provided:

    - Types, manufacturer, main technical data, and dimensional drawings of the transformers (T1, T-2) to be installed.

    - Types, manufacturer, main technical data, preliminary single-line diagrams, and dimensional drawings of the planned JVS-1 switchgear and 16PS-1X cabinets.

- APPENDICES:

  - List of project documents, their marking structure.

  - Number coding system for electrical cable lines.

  - List of abbreviations.

  - Harmonized cable coding table.

  - Technical specification (in English).

  - List of equipment manufacturers.

  - TP-16 power supply block diagram.

  - TP-16 equipment layout plan.

  - TP-16 KTP existing single-line diagram.

  - Technical data of existing transformers T-1, T-2.

  - General view of the existing KTP switchgear with transformers.

  - Technical data of the existing KTP switchgear.

  - Existing 6kV relay protection settings.

  - Existing KTP 0.4 kV protection settings.

  - Existing JVS-1 single-line diagram.

  - Preliminary single-line diagram of TP-16 KTP, JVS-1, 16PS-1X power supply.

  - Existing control diagrams for motors connected to JVS-1.

  - AMP principle control diagram.

  - TP-16 KTP principle control diagram.

  - Typical new JVS-1 cell diagrams.

Prepared by:

Electrical and Automation Department

Technical Control and Analysis Group                  		                      Algirdas Šarkinas Engineer	Expert

APPROVED BY:

Technical Control and Analysis Manager                                                                 Evaldas Lungys