1. General.

Perform procurement and installation according to Attachment 1 (Electrical Design OLP02829).

Commission works with the Owner.

2. Attachments.

Attachment 1 - Electrical Design   OLP02829

Attachment 2 - PROCEDURE FOR ACCEPTANCE OF ELECTRIC AND AUTOMATION EQUIPMENT AS FIT

FOR SERVICE

3. Description and specifics of work.

3.1. Description of work.

3.1.1. According to design (rev. ‘Approved’) provided by the Owner, the Contractor shall perform installation works.

3.1.2. Installation shall be performed keeping critical power users powered (only temporary switch-overs are allowed).

3.1.3. After installation, necessary commissioning, measurements and tests shall be performed as set forth in the Electrical Equipment Testing Standards & Scopes (Lith. Elektros įrenginių bandymų normų ir apimčių aprašas), and the Rules for the Installation of Electric Equipment (Lith. Elektros įrenginių įrengimo taisyklės). Test reports and other technical documentation shall be presented.

3.1.4. During commissioning, the following works must be peformed, including but not limited to:

3.1.4.1. accumulator battery capacity check with at least 5-hour test;

3.1.4.2. Measurement of UPS output voltage oscillograms in various switching modes (electronic bypass activation/deactivation, activation of power supply from battery packs, switching from battery power to operational power);

3.1.4.3.  Checking the discrete outputs of the UPS fault alarm.

3.1.5. After the installation work, the Contractor must perform functional tests in the presence of the Owner.

3.2. Special requirements (if any).

    - The Contractor shall prepare and agree with the Owner the UPS operating manual in accordance with the Owner’s procedures.

    - Before submitting a proposal, the Contractor shall visit the worksite and evaluate the scope of work.

    - In the event that the Contractor requests partial payments, the Contractor shall clearly define the corresponding milestones in the payment schedule submitted as part of the tender documentation. Payment for the milestone will be made only after complete performance of the particular milestone.

    - UPS must be with entered commissioning codes.

    - UPS must be with deactivated maintenance alarm function (may be with maximum delay period set).

3.3. Requirements for work execution and documentation.

3.3.1. After completion of works, the Contractor shall issue AS BULT design revision with all necessary documentation.

3.4. Qualification requirements for Contractor.

3.4.1. The Contractor and its subcontractors shall hold the following documents authorizing them to perform the respective works:

3.4.1.1. Certificates issued by National Energy Regulatory Council of the Republic of Lithuania for:

- Works related to operation of power network and units up to 1000V;

- Testing of power network and units up to 1000 V;

- Operation of power installations up to 1000V.

3.4.1.2. UPS commissioning works must be performed by Contractor holding qualification documents issued by manufacturer.

3.4.2. For the evaluation of the technical part of the proposal the Contractor shall provide:

3.4.2.1. Analysis of current situation and descriptions of works;

3.4.2.2. Work execution schedule. The schedule shall be divided into milestones, indicating whether the contractor or subcontractor will carry out the work. If works are carried out by several subcontractors, subcontractors shall be indicated for each milestone;

3.4.2.3. A list of designing and installation works of similar scope performed during the past five years;

3.4.2.4. List of subcontractors

3.4.2.4. In the commercial proposal, the costs of each milestone must broken down into labor, materials, and machinery.

4. Materials, equipment, and services to be provided by the Owner.

N/A

5. Materials, equipment, and services to be provided by the Contractor.

5.1. All materials and equipment required for the above works shall be provided by the Contractor.

5.2. All equipment and work tools needed to perform the works shall be provided by the Contractor.

5.3. The Contractor shall provide UPS and other materials required for realization of the design.

6. Requirements for work completion.

6.1. Handover of AS BUILT revision of the design;

6.2.  Installation of equipment;

6.3. Commissioning/startup;

6.4. UPS functional test.

7. Requirements for work acceptance.

The works shall be deemed fully completed after the Certificate on Electrical Equipment Fitness for Service has been issued in accordance with AB ORLEN Lietuva procedure (see Attachment 2), and the drawbacks specified in the certificate have been eliminated. Documents submitted by the Contractor shall include:

- USB with AS BUILT design drawings in PDF format. Each document listed in the project documentation and drawing registration shall be submitted as an individual file. File names must exactly match the document designation and include the corresponding revision number.

8. Requirements for work schedule.

Provisional schedule:

End of installation works – 1 Dec 2026.

Submission of reports/documentation - by 30 January 2027.