1. General.

Original design height of the stack – 125 m, current height (post-2003 maintenance) – 114 m. The outlet diameter of the stack – 4.8 m. The stack was built using perforated clay bricks bonded with composite cement mortar. Thermal insulation from mineral wool slabs and diatomic bricks was installed up to the height of 114 m. Refractory lining is made with firebricks bonded with heat-resistant mortar. Two aircraft warning platforms are installed on the exterior of the stack – one at an elevation of 75 meters, and the other at 112 meters. The ladder starts at 2 m above the ground and goes as high as 112.7 m. The ladder has safety cages. Cages are made from 50-60 mm steel strips. The top section of the stack has a stainless steel tip. The design lightning protection system includes stainless steel tip, lightning rod and grounding system. The stack includes two ports for connecting flue gas ducts at elevation +0.000.

During warning light replacement works, external inspection was performed, defects were identified and must be eliminated. Defects specified in UAB Dūmtraukis punch list No 2026/01.

2. Attachments.

- UAB Dūmtraukis PUNCH LIST No 2026/01

3. Description and specifics of work.

3.1. Description of work.

Works specified in UAB Dūmtraukis PUNCH LIST No 2026/01

3.2. Special requirements (if any).

The Contractor shall visit the site to assess installation conditions and requirements. The Contractor shall perform visual inspections using optical tools to identify potential work zones.

The Contractor shall ensure all actions maintain the quality and safety of the works.

Upon completion of the inspection and any associated works, the Contractor shall remove all tools, materials, and equipment from the Owner’s premises and leave the site clean, safe, and ready for use.

3.3. Requirements for work execution and documentation.

- The Contractor shall present OHS and waste management plan agreed with ORLEN Lietuva Quality, Labor Safety and Environmental Control Department;

- The Contractor be required to present method statement which will specify: work to be performed, work methods, material certificates, etc.;

- Contractor shall present the work execution schedule for each part of work hereunder separately.

3.4. Qualification requirements for Contractor.

To be considered eligible, the Contractor shall submit the following documentation as proof of qualification:

- A valid copy of the company’s registration certificate;

- A license or permit issued by the Ministry of Environment of the Republic of Lithuania, or an equivalent document issued by a competent authority in another country and recognized in Lithuania. The license must confirm the Contractor’s right to perform construction works in accordance with Technical Regulation for Construction STR 1.02.07:2012;

- A qualification certificate for a construction manager authorized to execute works of exceptional significance, or a comparable document issued in another country and recognized in Lithuania under STR 1.02.07:2012;

- A certificate issued by the National Energy Regulatory Council (VERT) of the Republic of Lithuania, confirming the Contractor’s right to perform stack repair works;

- Proof that all employees are certified for working at height;

- List of independently completed works during the last two years, their value.

4. Materials, equipment, and services provided by OWNER.

The Owner will provide the Contactor with electricity and water.

5. Materials, equipment, and services provided by Contractor.

All materials, equipment, machinery required for the works shall be provided by the Contractor.

Premises (containers) for employees to rest and change, bio-toilets. The location of containers and bio-toilets to be agreed with the manager of respective organizational unit.

6. Requirements for work completion.

- Works shall be deemed completed after presentation of technical documentation and site handover and acceptance statement.

7. Requirements for work acceptance.

Works shall be deemed completed after presentation of technical documentation and site handover and acceptance statement.

8. Requirements for work schedule.

Expected date of works: May to July of 2026 (may change).