AB ORLEN LIETUVA

SCOPE OF WORK AND REQUIREMENTS

FOR FEASIBILITY STUDY OF INSTALLATION OF BATTERY ENERGY STORAGE SYSTEM (BESS) IN SOLAR FARM OF AB ORLEN LIETUVA

02 March 2026

Juodeikiai Vill., Mažeikiai Distr. Municipality

## 1. Description

Crude oil refinery of AB ORLEN Lietuva (hereinafter, the Owner, OL) is equipped with:

Two steam turbines, 80 MW each;

Four solar farms within OL with total nominal capacity of 42.2 MWp. This total capacity is distributed across four solar farms as follows: SE-1 – 29.98 MWp, SE-2 – 4.64 MWp, SE-3 – 2.8 MWp, SE-4 – 4.99 MWp.

All electricity regenerated by solar farms is intended to satisfy internal energy needs of the refinery. Electricity is not transmitted to LITGRID (transmission system operator).

Solar farms SE-1, SE-2, SE-3, and SE-4 are integrated into OL power system via dedicated transformers and 6 kV switchgear cubicles.

The refinery’s electricity demand is covered by in-house Power House and solar farms SE-1, SE-2, SE-3, SE-4 as well as external transmission grids.

## 2. Purpose

The purpose of feasibility study is to evaluate technical and economical possibilities to install battery energy storage system (BESS) integrated with power farms of the refinery utilizing only existing infrastructure of solar farms.

## 3. Tasks

Evaluate existing power infrastructure of solar farms SE-1, SE-2, SE-3, SE-4 and possibility to integrate energy storage devices.  Existing power infrastructure of solar farms consists all electrical equipment upstream connection cubicles in refinery 6 kV switchgears/substations, including PV modules, inverters, 0.8/6 kV transformer substations (16 pcs), cables, etc.

Analyze in-house power consumption and generation dynamics, select BESS of required power and capacity.

Define the principles of control for new BESS in in-house grid.

After key technical parameters are defined, perform preliminary estimation of CAPEX (with 20 % accuracy).

Evaluate and quantify potential benefits of BESS:

- Preliminary optimization of capacity ordered from Lithuanian power transmission system operator LITGRID;

- Preliminary optimization of the price of purchased electricity;

- Possibility and conditions for optimizing the provision of system services (mFRR, FCR).

- A brief assessment of possible scenarios and the benefits that BESS would provide for electricity supply reliability in the event of blackout. In the event of blackout, the priority would be the restoration of generation at in-house Power House with steam turbine.

## 4. Scope of work

### 4.1. Analysis of existing infrastructure

Evaluate solar farm wiring diagrams, power flows, reserves and infrastructure limitations.

Evaluate the impact of BESS on automatic load transfer activation and relay protection diagram functioning.

Define potential places for connection of BESS and evaluate required modifications to the grid (connectors, cables, protectors, control systems, etc.).

Develop single line diagrams for connection of BESS installations to existing infrastructure of solar farms.

Select preliminary places for installation of BESS and cabling (to be agreed with OL).

- NOTE: The Owner expects that the Contractor will focus on the most cost‑optimal and rational solution.

### 4.2. Power demand and generation analysis

Taking into account OL electricity consumption and generation profiles, the Contractor shall:

Select the most suitable power storage technology (Li-ion, LFP, NaS, flow battery, etc.). Provide the reasoning and justification for the proposed solution.

Determine the optimal power (MW) and capacity (MWh) of the storage system(s). Provide the reasoning and justification for the proposed solution.

Based on the selected storage technology, power, and capacity, provide a list of potential suppliers. Provide preliminary time-line for delivery of equipment, including control system.

### 4.3. Control system integration concept

Evaluate whether new BESS can be integrated into existing SCADA of solar farms.

Describe and/or schematically present the preliminary control logic/algorithm (charging, discharging, load balancing, emergency mode). Provide examples of charging/discharging cycles over a 24‑hour period (under various scenarios).

### 4.4. Evaluation of required CAPEX

Quantify preliminary engineering, procurement and construction (EPC) budget (with 20 % accuracy).

Develop CAPEX summary by key cost groups.

### 4.5. Economic benefit and payback analysis

Calculate annual savings and present the savings broken down by quarter, considering the following potential benefits:

- Optimization of capacity ordered from Lithuanian power transmission system operator LITGRID (capacity cost component, ancillary services cost component);

- Optimization of the price of purchased electricity, by charging BESS when market price is low and/or OL solar farms are generating surplus energy, and discharging when the market price is high and/or OL solar farms are not generating or generating minimally. It is important to note that electricity from solar farms and BESS cannot be sold on the market;

- Optimizing the provision of system services (mFRR, FCR);

- Other benefits (defined by the Contractor).

Assess annual BESS operation and maintenance (O&M) costs.

Determine preliminary BESS service life.

Evaluate the possibility to use BESS to restart the Power House after grid blackout.

### 4.6. Conclusions and recommendations

- Summarize the findings of technical and economic analysis.

- Present conclusions and recommendations concerning technical feasibility, financial benefit and risks.

- Present final feasibility study report (PDF) with all attachments.

## 5. Additional information

- After contract is signed, feasibility study should be completed in 20 weeks.

- Contractor shall present a detailed feasibility study execution schedule.

- The Contractor shall present a list of information/data required for the study (in XLSX format);

- The results shall be presented in Lithuanian language: signed feasibility study report (in PDF format), attachments in PDF format and editable native formats such as DOC, XLSX, DWG, etc.