1. General.

Terms and definitions used herein:

Onshore LDS – onshore leak detection system.

Import regime – regime when Būtingė Terminal pumps crude to ORLEN Lietuva.

Export regime – regime when ORLEN Lietuva pumps crude to Būtingė Terminal.

OL – ORLEN Lietuva (Owner).

The following works shall be performed:

- Designing an onshore LDS for the pipeline Būtingė Terminal–Lenkimai–Skuodas–ORLEN Lietuva.

- Installing the onshore LDS as per design.

- Testing and commissioning the onshore LDS.

- Training Owner’s personnel.

2. Attachments.

AVS1_Kibernetinio saugumo reikalavimai (OL-TR-IR-021 rev01) (cybernetic security requirements).

AVS2_Esamos sistemos architektūra (architecture of the existing system).

AVS3_Kranto LDS tikslumo  reikalavimai (precision requirements for LDS).

AVS7_AVS programavimo konfiguravimo aktas (ACS programming-configuration report).

AVS8_Reikalavimai kompiuteriams (requirements for computers).

AVS9_Reikalavimai dokumentacijai (requirements for documentation).

AVS10_Technical Query

Priedas_SOW_OLP02652_PVA_rev0 2024-11-22 and additional attacments

3. Description and specifics of work.

3.1. Work description.

3.1.1. A brief description of the current situation.

Pressure is measured at at the following four points (before and after the shutoff valves) (hereinafter – measuring points):  in OL pump house No 25, Skuodas intermediate valve station, Lenkimai intermediate valve station and Būtingė Terminal.  Pressure data is transmitted to Modicon M340 controllers located at each measuring point.  Computer KNPS1 collects data from all four controllers via an optic network, processes the data, detects leaks, calculates the location of the leak, etc.  A certain amount of data is archived in the KNPS2 computer. Būtingė Terminal operators can see data, graphs, messages, etc. on the KNPS_oper computer. The preliminary architecture of the existing onshore LDS is presented in Attachment ‘AVS2_Esamos sistemos architektūra’.

p.s. It should be noted that communication between Būtingė Terminal, valve stations and OL pump houses is conducted via a single physical 4 core fiber optic cable.  These fibres are also used for other control systems. This cable does not have any more free core fibers.

3.1.2. Designing.

Designing a new onshore LDS for the pipeline Būtingė Terminal–Lenkimai–Skuodas–ORLEN Lietuva. Scopes of work, design requirements and other information for design are indicated in Attachment ‘Priedas_SOW_OLP02652_PVA_rev0 2024-11-22’ (hereinafter – scope of design).

p.s. Currently used pressure transmitters are UNIK 5000 PTX59J2-TC-A3-CA-H4-PR.

Requirements for the newly designed onshore pipeline leak detection system:

The leak detection system shall inform the operator when a leak occurs in the pipeline. The onshore LDS system shall have a separate dedicated onshore LDS computer.

It is not planned to replace the field instruments and the points of their tie-ins, except where it is not possible to achieve the precision needed for leak detection.  All replacements shall be agreed with the Owner at the time of design.

If necessary, the Contractor shall design and supply a new cabinet for computers and other equipment.  If a new cabinet is to be designed, it shall be equipped with a flue gas detection system. This requires extending the existing system.

Requirements for computers and software are provided in Attachment ‘AVS8_Reikalavimai kompiuteriams’

The new system shall be operational in both import and export regimes.

A leak message shall be displayed on the operator's computer within 5 minutes of the occurrence of the leak.

Leak, fault and similar messages shall be archived and shall be available for at least 5 years.

The minimum information to be provided in the message: the date, time, location of the leak from the nearest measuring point, the intensity of the leak (m3/h), the probability of the leak being detected (%).

The message of a detected leak (provided within 5 minutes of the leak) shall contain the following information:

Date and time;

Leak place from the nearest measuring points (km);

Intensity (liters per second and m3/h);

Probability of detected leak (0 to 100%).

All messages generated by the system without actual leak present shall be considered erroneous. The number of such messages shall be not more than one per month.

All leak detection messages shall be generated by the system automatically.

Accuracy requirements for the onshore LDS are set out in Attachment ‘AVS3_Kranto LDS tikslumo reikalavimai’.

Design related to the leak detection system on the main pipeline is provided in Attachment 6 to the Scope and Requirements for the PCI Design.

The system shall be possible to expand by connecting other main pipelines to such.

The leak detection system shall be good for all sorts of crude oils or petroleum products with their density ranging from 0.7 to 1.0 kg/liter.

3.1.3. Installation and testing of the onshore LDS.

Installation of the new onshore LDS following successful factory acceptance tests (dismantling the existing equipment, installing new equipment, checking SAT/SIT loops, etc.)

Performing programming and testing related to changes (if any designed) made to the flue gas detection system.

3.1.4. Commissioning and testing. Commission and testing of the new onshore LDS shall be attended by the Contractor for immediate rectification of faults if any.

3.1.5. Handing the system over to the Owner.  Training the operators, maintenance personnel.

3.2. Special requirements (if any).

3.2.1. For 5 years following the upgraded/new system installation, commissioning date, the Contractor shall fix any flaws or defects, where such exceed the minimal technical parameters indicated in the table below, free of charge. The defects shall be eliminated (fixed) within 3 months from the date of the claim submitted by e-mail.

3.2.2. If the Contractor is going to perform works in milestones, the Contractor shall agree with the Owner on the time and possibility to perform these works.   Furthermore, the Contractor shall specify in its proposal the preliminary dates and duration of separate milestones, the scope of planned work and outline the essential aspects of the work.

3.2.3. If the Contractor expects milestone payments, its proposal shall include a milestone payment schedule (e.g. after approval of design, after FAT, etc.) with a maximum of 5 payments.

3.2.4. The Contractor’s proposal shall include a detailed cost estimate split into:

Engineering (designing);

Materials;

Programming;

Installation;

Submission of documentation.

3.3. Requirements for work execution and documentation.

3.3.1. In addition to the documentation specified in the Scope of Design Work, the Contractor shall submit the documentation indicated in Attachment ‘AVS9_Reikalavimai dokumentacijai’.

3.3.2. The Contractor shall submit technical questions, proposals, etc. in the form provided in Attachment ‘AVS10_Technical Query’.

3.3.3. Requirements for documentation and completion of works are set out in Paragraphs 3.3, 6, 7.

3.3.4. The Contractor (or subcontractor) carrying out installation work in operating electrical facilities shall have the authorizations necessary for such work (in accordance with the normative acts of the Republic of Lithuania).

3.4. Qualification requirements for Contractor.

3.4.1. The Contractor shall be experienced with this type of projects.  The Contractor shall submit a list of similar projects completed in the last 3 years.

3.4.2. The Contractor shall present the list of subcontractors (if any) and copies of their certificates granting the right to perform such work as required by the applicable legislation.   All subcontractors are subject to Owner’s approval.

4. Materials, equipment, and services to be provided by the Owner.

## The Owner will not provide any materials, equipment or services.

5. Materials, equipment, and services to be provided by the Contractor.

5.1. The Contractor shall provide all materials required for the implementation of the project.  The Contractor shall also supply materials not included in the specification but necessary to complete the project in accordance with this Scope of Work. The proposal shall cover all works that are described or specified in the drawings, specifications, scope of design work, etc. Any minor works not specified in the drawings or specifications but necessary to ensure work functionality and completeness shall be considered as included in the proposal price.

5.2. At least a 3-year warranty shall be provided for the hardware.

The supplied equipment shall have at least a 5-year life cycle.

5.3. All supplied hardware shall be new. If several versions are available, the latest upgraded version shall be used.

5.4. All the equipment and materials supplied shall have the necessary certificates and quality documents (specified in the Technical Requirements);

5.5. The Contractor’s scope shall include FAT, SAT and SIT procedures.

5.6. The Contractor’s scope shall include the testing of the system required for the acceptance of the new onshore LDS by the Owner.

5.7. The Contractor shall provide an optimal quantity of spares for rapid restoration of system functionality to be delivered to the Owner immediately after the handover of the onshore LDS to the Owner.

5.8. Design errors affecting the testing, installation, handover of the system shall be rectified by the Contractor at its own expense and without affecting the work schedule.

5.9. Costs associated with the clearance of materials shall be included in the proposal.

5.10. Equipment damaged during the testing or handover of the onshore LDS shall be immediately replaced at the Contractor’s expense (without the use of the spares referred to in Paragraph 5.7).

6. Requirements for work completion.

6.1. Review of proposed solutions and agreement with the Owner.

6.2. Development of the design.

6.3. Installation of equipment.

6.4. Commissioning.

6.5. Removal of dismantled equipment (within the scope of the design).

6.6. Presentation of the following in soft version (USB) after completion of works:

6.6.1. Installed equipment configuration software (if any was used);

6.6.2. Controller configuration files, backup copies, databases, etc.;

6.7. Presentation of the following in soft version (USB) or hard copy after completion of works:

6.7.1. Newly created (or modified) software users, passwords, network addresses, settings, other information, which is required for further maintenance and troubleshooting;

6.7.2. Newly installed (or upgraded/expanded) software licenses.

6.8. Contractor shall provide training for:

6.8.1. Process personnel, in case of any changes in the operation of the system or implementation of an important innovation, etc.

7. Requirements for work acceptance.

7.1. The works shall be considered fully completed when, in accordance with the procedure applicable by ORLEN Lietuva, an ACS Programming/Configuration Work Handover and Acceptance Statement (Attachment AVS7 ‘ACS Programming-Configuration Report’) is issued and all deficiencies specified therein rectified. Documentation submitted by the Contractor must also include a USB flash drive containing AS BUILT design drawings in .dwg format as well as data needed for the completion of works (Section 6).

7.2. All design drawings shall be marked AS-BUILT, signed by the Contractor and handed over to the Owner (1 electronic copy and 2 hard copies). The Contractor shall submit to the project manager the detailed engineering design on a USB stick prepared for transfer to the archive in accordance with the OL archiving requirements.

7.3. Upon completion of the works, the Contractor shall deliver the technical documentation in accordance with the requirements of the normative acts of the Republic of Lithuania and the Owner.

8. Requirements for work schedule.

Contractor shall present its detailed work and payment milestone schedule detailed (split) by years, months and works performed. Payment for materials and works will be executed based on such schedule.

Designing - during the calendar year of 2025.

Implementation works shall be completed and handed over the Owner until 2026 may 16.

No longer needed equipment shall be dismantled, documentation shall be submitted in two months after the startup.