1. General.

1.1. It is required to perform maintenance works on power equipment of Operations Subdivision           No 3 (OS-3) at crude oil refinery of AB ORLEN Lietuva (hereinafter, the Owner) under work packages R_ERP07-GP-3 and R_ERP08-GP-3.

1.2. Submit maintenance, testing / measuring reports / statements.

NOTE: All works shall be executed under approved Permit to Work. LOTO shall be performed in accordance with the Owner’s procedures. No work on energized equipment is allowed unless separately authorized in writing. Contractor and its staff shall comply with the Owner’s requirements and procedures made available at: ORLEN Lietuvhttps://www.orlenlietuva.lt/EN/ForBusiness/DocumentsForContractors/Pages/Occupational-Safety-and-Health-Documents.aspxa

2. Attachments.

- R_ERP07 GP-3_Attachments

- R_ERP07-GP-3 works contractors_mhrs_EUR;

- R_ERP07-GP-3_Job list;

- R_ERP08-GP-3_Attachments;

- R_ERP08-GP-3 works contractors_mhrs_EUR;

- R_ERP08-GP-3_Job list.

3. Description and specifics of work.

3.1. Job list:

- TPP-17 KTP-1 cabinet inspection / maintenance;

- SGĮ-1 TP-16 KTP cabinet inspection / maintenance;

- SGĮ-2 TP-74 KTP cabinet inspection / maintenance;

- CKS TP-15 KTP cabinet inspection / maintenance;

- TPP-7 0.4kV busbar section maintenance;

- TPP-30 0.4kV busbar section maintenance;

- Installation of busbar insulation spacer for TP-33 (SDN-3242, SDN-3241, SDN-3243);

- Installation of busbar insulation spacer for TPP-18 (SDN-3246, SDN-3247, SDN-3248);

- Installation of busbar insulation spacer for TPP-21 JVS-4 (SDN-3280).

3.2. Detailed description of works:

3.2.1. TPP-17 KTP busbar sections (cabinets) - inspection, maintenance, el. measurements

KTP switchgear has two separate sections, 11 cabinets.

Scopes of work:

Clean switchgear busbars, insulators, contact blades, and terminals removing dust and old grease, and assessment of their condition;

Replace insulators, terminals as needed according to condition (chips, cracks, etc.), notify the Owner before replacement;

Tighten bolted connections of switchgear busbar section power and control circuits and other components, and repair identified defects;

Inspect and tighten power and control cable terminations at terminal blocks;

Lubricate contact blades using electrotechnical contact grease;

Inspect busbar insulation, including measurements with insulation resistance meter.

NOTE: No repair, testing, or electrical measurements will be required for the withdrawable part of switchgear cabinets (incoming circuit breakers, bus-tie circuit breakers, and circuit breakers/contactors of power users).

Documents to be submitted to the Owner:

Completed work (maintenance) statements, el. measurement reports.

TPP-30 KTP busbar sections (3 cabinets) and conductor - inspection, maintenance, el. measurements

KTP switchgear has two separate sections, 3 cabinets, 2 conductors to JVS-1.

Scopes of work:

Clean switchgear busbars, insulators, contact blades, and terminals removing dust and old grease, and assessment of their condition;

Inspect, clean, tighten the conductor, repair identified defects;

Replace insulators, terminals as needed according to condition (chips, cracks, etc.), notify the Owner before replacement;

Tighten bolted connections of switchgear busbar section power and control circuits and other components;

Inspect and tighten power and control cable terminations at terminal blocks;

Lubricate contact blades using electrotechnical contact grease;

Repair identified defects (notify the Owner before repair);

Inspect busbar insulation, including measurements with insulation resistance meter.

NOTE: No repair, testing, or electrical measurements will be required for the withdrawable incoming and bus‑tie circuit breakers of switchgear panels.

Documents to be submitted to the Owner:

Completed work (maintenance) statements, el. measurement reports.

3.2.3 Elimination of unsafe workplaces (SDN) - installation of busbar insulation spacers between sections in power control panels (switchgears)

Scopes of work:

For enclosed‑type MCC switchgears (comprised of two separate busbar sections):

In switchgears, install approx. 1–2 mm thick electrotechnical textolite spacers between the busbars of individual sections. Install the spacers by loosening bolted connections between the cabinets and mechanically expanding them. After installing the spacers, tighten bolted joints interconnecting the cabinets.

For open‑type MCC switchgears:

In switchgears, install approx. 1–2 mm thick electrotechnical textolite spacers between the busbars of individual sections. Install the spacers on individually selected /designed textolite plate mounting structures.

Documents to be submitted to the Owner:

Completed work (maintenance) statement.

3.2.4. TP-74 KTP 0.4kV complex transformer substation maintenance

KTP panel has 8 cabinets, 19 withdrawable trolleys

Scopes of work:

Clean the busbars from dust, clean contact connections from old grease, lubricate with new grease;

Clean, inspect insulators, replace as required according to condition;

Evaluate the condition of commutation devices (circuit breakers, contactors, thermal relays), control circuit elements (relays, terminals, wires), replace as required according to condition;

Inspect outgoing cable line junction boxes, replace as required according to condition;

Inspect the connections (terminations) of outgoing cables;

Inspect the racking mechanism (trolley);

Perform functional proof tests of electric motors and other control schemes / circuits;

Testing the insulation of the panel, in accordance with the requirements of IEC 61439.

Documents to be submitted to the Owner:

Completed work (maintenance) statements, inspection/testing reports.

3.2.5. TPP-17 KTP-1 0.4kV complex transformer substation maintenance

KTP-1 panel has 9 cabinets, 14 withdrawable trolleys

Scopes of work:

Clean the busbars from dust, clean contact connections from old grease, lubricate with new grease;

Clean, inspect insulators, replace as required according to condition;

Evaluate the condition of commutation devices (circuit breakers, contactors, thermal relays), control circuit elements (relays, terminals, wires), replace as required according to condition;

Inspect outgoing cable line junction boxes, replace as required according to condition;

Inspect the connections (terminations) of outgoing cables;

Inspect the racking mechanism (trolley);

Test the circuit breakers;

Perform functional proof tests of electric motors and other control schemes / circuits;

Testing the insulation of the panel, in accordance with the requirements of IEC 61439.

Documents to be submitted to the Owner:

Completed work (maintenance) statements, inspection/testing reports.

3.2.6. TP-15 KTP 0.4kV complex transformer substation maintenance

KTP panel has 7 cabinets, 14 withdrawable trolleys.

Clean the busbars from dust, clean contact connections from old grease, lubricate with new grease;

Clean, inspect insulators, replace as required according to condition;

Evaluate the condition of commutation devices (circuit breakers, contactors, thermal relays), control circuit elements (relays, terminals, wires), replace as required according to condition;

Inspect outgoing cable line junction boxes, replace as required according to condition; Inspect the connections (terminations) of outgoing cables;

Inspect the racking mechanism (trolley);

Perform functional proof tests of electric motors and other control schemes / circuits;

Testing the insulation of the panel, in accordance with the requirements of IEC 61439.

Documents to be submitted to the Owner:

Completed work (maintenance) statements, inspection/testing reports.

3.2.7. TP-16 KTP 0.4kV complex transformer substation maintenance

KTP panel has 9 cabinets, 20 withdrawable trolleys

Clean the busbars from dust, clean contact connections from old grease, lubricate with new grease;

Clean, inspect insulators, replace as required according to condition;

Evaluate the condition of commutation devices (circuit breakers, contactors, thermal relays), control circuit elements (relays, terminals, wires), replace as required according to condition;

Inspect outgoing cable line junction boxes, replace as required according to condition; Inspect the connections (terminations) of outgoing cables;

Inspect the racking mechanism (trolley);

Perform functional proof tests of electric motors and other control schemes / circuits;

Testing the insulation of the panel, in accordance with the requirements of IEC 61439.

Documents to be submitted to the Owner:

Completed work (maintenance) statements, inspection/testing reports.

4. Requirements for performance of works, documents and submission of proposal

Perform all works in compliance with the Owner’s requirements;

Present testing/measuring reports for the repaired equipment;

Obtain a permit for operation from the Technical Inspection and Analysis Group of the Electrical and Automation Department;

Plan to have a reserve of personnel (approximately 10–20%) in case of need.

NOTE: Before submitting a proposal, the Contractor is required to visit the Owner’s objects listed in the work summary and carry out an on‑site assessment of the scope of work, required resources, equipment design features, and other relevant factors.

5. Qualification requirements for Contractor

Valid certificate issued by the National Energy Regulatory Council for operation of energy facilities (power equipment) authorizing performance of the works specified in this SOW.

Certificates issued for electrical works by the National Energy Regulatory Council to be held by legal entities for work at AB ORLEN Lietuva:

Operation of power network and facilities with voltage up to 1000 V;

Testing of power network and facilities of up to 1000 V;

Operation of special el. power installations;

Operation of electric wiring of up to 1000 V;

NOTE: The certificate must correspond to the scope of works performed and minimum required voltage level.

6. Materials, equipment and services to be provided by the Owner

Energy resources (electricity) in the Contractor’s work area: upon the Contractor’s request, electricity in the Contractor’s work area shall be provided free of charge. Contractor’s electrical equipment shall be connected to ~220V and ~380V mains in accordance with AB ORLEN Lietuva Procedure for Temporary Powering of Electrical Equipment BE-16, upon the presentation of request and issue of the Statements on the Limits of Responsibility.

Materials for installation of spacers (electrotechnical textolite) and examples for installation;

Cable lugs for repair of cable terminations;

Electrical conductors, lubricant for contact blades;

Terminals;

Power commutation and protection devices, spares.

7. Materials, equipment and services to be provided by the Contractor.

Work (maintenance) and documentation quality assurance, proposed solutions for unforeseen problems;

Aerosol cleaners, lubricants / grease, etc.

8. Requirements for work completion

The Contractor must submit to the Owner the documents specified within this SOW, with drawbacks (if any identified by the Owner during the review) corrected;

The Contractor must submit all other required documents, including statements of materials actually used up for its work;

The Contractor must return any materials provided to it that were not used during the works, restore /clean the work site, collect and remove all waste generated during the performance of the works;

The Contractor must fix all identified defects.

NOTE: Completion of work shall be certified by work handover and acceptance statement signed between the Owner and the Contractor.

9. Requirements for work acceptance

Works shall accepted in accordance with the Owner's procedures.

Works shall be deemed completed after requirements under Par. 8 above are fulfilled and all equipment hereunder is tested under load (after startup).

10. Requirements for work schedule

Works are planned for AB ORLEN Lietuva Refinery Turnaround 2027 (preliminarily, spring of 2027 - the start and duration of the works will be specified later). Due to operational needs, work schedules may be subject to change.

Work mode: in 1 eleven-hour shift 7 days/week.

Preliminary period: April - May 2027.

Work time on each specific site/location (switchgear) within the specified period will be agreed individually according to technical possibilities.

NOTE: Partial payments as requested by the Contractor will be made only if the Contractor specifies in advance the milestones subject to payments in the schedule presented by it for the tender (i.e. if the Contractor presents a milestone payment schedule).