- General.

  - The Power House steam turbine PT-80/100-130/13, tag No. T-2, manufactured by Leningradsky Metallichesky Zavod (Russia), serial No. 1588, was produced in 1980 and has been in operation since 1981.

To ensure reliable operation and timely detection and elimination of defects, in accordance with the manufacturer’s recommendations, operational experience, and accumulated operating hours (43,800 hours), the steam turbine T-2 is subject to a major overhaul. During this overhaul, defects that could not be eliminated during the 2017 overhaul due to the unavailability of spare parts shall be rectified.  In addition, other works listed below will be carried out in order to improve the efficiency, reliability, and operational performance of the turbine.

  - The turbogenerator TVF-120-2Y3, tag No. TG‑2, was manufactured by Sibelektrotyazhmash (Novosibirsk, Russia) in 1980, serial No. 179.  Manufactured in 1980, serial number 179. The turbogenerator TG-2 was last overhauled in 2017. According to the manufacturer’s recommendations, major overhauls of the generator shall be performed every 4–5 years. To ensure continued reliable operation, it is necessary to perform a major overhaul of turbogenerator TG-2.

- Attachments.

  - Attachment A – Scope of Work for Overhaul of Steam Turbine T-2.

  - Attachment B – Scope of Work for Overhaul of Turbogenerator TG-2.

  - Attachment C – Turbine and piping drawings, 16 sheets.

3. Description and Specifics of the Works.

3.1. General requirements.

Overhaul of the Power House steam turbine T-2 (PT-80/100-130/13) and turbogenerator TG-2 (TVF-120-2Y3).

3.2. Work description.

    - Perform a major overhaul of steam turbine T-2 in accordance with the detailed scope of works provided in Attachment A.

    - Perform a major overhaul of turbogenerator TG-2 in accordance with the detailed scope of works provided in Attachment B.

    - Prior to commencement of the overhaul, the Owner, together with the Contractor, shall carry out an inspection of the turbine and the generator. The Contractor shall prepare and submit a work execution plan for review and approval by the Owner.

    - After disassembly of the turbine control system, removal of the turbine cylinder covers, and disassembly of the generator assemblies, a joint commission established by the Owner and the Contractor shall perform defect inspection of the turbine control system, flow (cartridge) section, and generator assemblies.

    - Following the defect inspection of the steam turbine and generator assemblies, a defect and measurement report shall be prepared. Based on the inspection results, the joint commission of the Owner and the Contractor shall submit conclusions and recommendations regarding the scope and methods of the required repair works, the list of agreed works, and delivery schedules for spare parts and materials not supplied by the Owner.

    - Carry out inspection and evaluation of the condition of the inter-turbine piping suspension system (see drawings in Attachment C), including:

- High-pressure crossover pipelines, drawing Б-1278491СБ;

- Medium-pressure crossover pipelines, drawing Б-1278512СБ;

- Piping to high-pressure pre-heaters, drawing Бу-1279809СБ;

- Piping to low-pressure pre-heaters, drawing Б-1279552СБ;

- Extraction steam pipelines, drawing Б-1280151Сб;

- Steam pipelines to TP-1 and TP-2.

3.3. Requirements for work execution and documentation.

    - Repair documentation for the turbine, generator, and piping shall be compiled and submitted separately. The scope of documentation for works performed on the turbine and generator shall include the following:

a) Punch lists for the turbine and generator prepared after disassembly and inspection;

b) Report on the scope of completed repair works;

c) List of applicable normative technical and technological documentation;

d) Steam turbine control system characteristics compiled after completion of repairs;

e) Generator test records, reports and conclusions;

f) Summary (bill) of materials and spare parts used during the repair;

g) Material quality certificates and passports;

h) Repair logbooks and reports for assemblies;

I) Quality certificates for parts;

j) Punch lists and conclusions of non-destructive testing (NDT) of welds, including mechanical testing, magnetic particle testing, or dye penetrant inspection;

k) Alignment records;

l) Static and dynamic balancing reports;

m) Work handover and acceptance statements;

n) Inspection and measurement reports for individual assemblies, including verification of external dimensions;

o) Welding documentation;

g) Other documentation as agreed separately between the Owner and the Contractor.

    - The Contractor shall ensure cleanliness and good housekeeping of the work areas and surrounding territory. At the end of each shift, the Contractor shall clean and organize the worksite and segregate and remove all waste generated during the works to locations agreed with the Owner, in accordance with AB ORLEN Lietuva Waste Management Rules.

    - Due to the design and construction of the steam turbine and the turbogenerator, the Contractor shall perform all repair works at the turbine installation site. An exception shall apply to the turbine and generator rotors: upon disassembly, the rotors may be repaired at the Contractor’s workshop facilities.

    - The Contractor shall submit all repair documentation in the Lithuanian language. Documents in a foreign language are permitted only for material manufacturers’ passports and certificates.

    - The Contractor shall prepare and submit a list of parts and components recommended for replacement during the next major overhaul.

    - The Contractor shall provide a warranty for the equipment or assemblies within the scope of the Contractor’s services for a period of not less than 12 months.

3.4. Special requirements (if applicable).

3.5. Qualification requirements for Contractor.

3.5.1. Valid certificates issued by the State Energy Regulatory Council, granting the right to perform repair works on turbines and electrical generators with a capacity exceeding 1 MW.

3.5.2.   At least 5 years of experience in performing major overhauls of steam turbines PT-80/100-130/13 and turbogenerators TVF-120-2Y3, or of technically equivalent equipment with comparable parameters.

4. Materials, equipment and services provided by the Owner.

4.1. The Owner will perform insulation works.

4.2. For the performance of all repair works at height, the Owner will provide scaffolding installation and dismantling services.

4.3. Connection and disconnection of control and measurement instrument cables at the Central Control Room, in accordance with the approved work schedule or upon the Contractor’s request.

4.4. The Owner will perform temporary electrical connections in accordance with the procedures established by the Company. The Owner will allow connection to technical compressed air and water supply pipelines.

4.5. The Owner will disconnect and prepare the turbine for overhaul according to the approved repair schedule.

4.6. The Owner shall provide available turbine drawings, logbooks, and technical passports.

4.7. An overhead crane located in the turbine hall, with a lifting capacity of 50 tons, will be provided for turbine and generator repair works, without an operator.

5. Materials, equipment, and services provided by the Contractor.

5.1.     The Contractor shall perform minor and single-item machining works, including turning, grinding, milling, and drilling.

5.2.      The Contractor shall perform machining and grinding of large parts and arrange their transportation to another workshop or company, where required (e.g. orifices).

5.3.    The Contractor shall dismantle threaded, keyed, and locking connections, including cases where stud threads are damaged, by drilling out damaged studs, removing stud remnants, repairing bores, and restoring threaded connections.

5.4. 	The Contractor shall perform post-weld heat treatment (PWHT) of welded joints where required, in accordance with the approved Welding Procedure Specification (WPS) or design documentation.

5.5. 	The Contractor shall perform all necessary preparatory and finishing works, shall participate in commissioning and startup activities, and shall provide stand-by attendance during test runs.

5.6. 	The Contractor shall provide all equipment, tools, and devices required for the execution of the works, including local lighting.

5.7. 	The Contractor shall supply all materials and equipment required for PWHT of welds.

5.8. 	The Contractor shall have a video camera for assessing the cleanliness of pipelines, prior to closing turbine casings and welding pipelines, in order to ensure that foreign objects or contamination will not damage rotor blades.

5.9. 	The Contractor shall procure or fabricate all required metal blanks, small items, and fastening materials, including supports, hangers, steel structures, rolled steel profiles, various nozzles, etc.

5.10. The Contractor shall supply materials for the repair of steam turbine T-2 and turbogenerator TG-2, as specified in Attachment A and Attachment B.

5.11. 	The Contractor shall supply all auxiliary and consumable materials, including grinding and cutting discs, propane, oxygen and other gases, cleaning agents, as well as welding consumables (electrodes, welding wire, etc.).

5.12.   The Owner will supply energy resources (compressed air, process water, electricity) to the Contractor free of charge at the worksite upon the Contractor’s request. Connection of the Contractor’s repair equipment to ~220 V and ~380 V power supply, compressed air, and process water systems shall be carried out based on a requisition submitted at the Central Control Room.

5.13. 	The Contractor shall be responsible for internal transportation of spare parts, equipment, and tools within the territory of OL.

5.14. 	The Contractor shall provide operators for the overhead crane.

6. Requirements for work acceptance.

6.1.     Final acceptance of the works shall be carried out by a commission appointed by the Owner or by an authorized representative of the Owner, in the presence of the Contractor’s responsible representative.

6.2. 	The works shall be deemed completed provided that all of the following conditions are met:

a) The works have been fully completed in accordance with the agreed scope of work;

b) The turbogenerator has successfully completed a 48-hour post-overhaul test run. Post-overhaul acceptance criteria:

• Relative shaft vibration level (X, Y) at bearings No. 1-6: not exceeding 120 μm (S1-165; B1-260);

• Absolute vibration level at measurement points No. 1-6: not exceeding 2.8 mm/s (S-4.5; B-11.2);

• Axial displacement at measurement points No. 1-3: not exceeding ±0.4 mm (S -0.9 / +1.4; B -1.2 / +1.7);

c)  Complete overhaul documentation has been submitted to the Owner.

6.3.    Final acceptance of the steam turbine and the turbogenerator after overhaul shall be carried out jointly by the Owner and the Contractor upon confirmation that, during testing and trial operation, the turbine and the generator comply with all technical requirements, and successfully pass thermal-performance express tests. The acceptance results shall be recorded in the final repair documentation.

6.4. 	The Contractor shall provide a warranty for the equipment or assemblies within the scope of the Contractor’s services for a period of not less than 12 months.

7. Requirements for work schedule.

7.1.   The preliminary start date of the overhaul works is planned for the first half of 2028.

7.2. 	The allocated duration for the overhaul of the steam turbine and the turbogenerator is 90 calendar days. The total repair period, including preparatory works, is 120 calendar days. For the tender, the Contractor shall prepare and submit a detailed work execution schedule for the turbine and generator overhaul works, with the works commencing from day ‘X’.

The Contractor shall submit a fixed-price cost estimate by completing the price breakdowns provided in the Attachments hereto. The fixed price shall include mobilization and demobilization costs, equipment and machinery costs, and labor costs.

Considering that the scope of works may be subject to adjustment during the overhaul, the Contractor shall additionally submit unit rates and hourly rates.