1.  General.

AB ORLEN Lietuva with its headquarters established at Mažeikių str. 75, Juodeikiai Village, LT-89467 Mažeikiai District, Lithuania (hereinafter, the Owner) is looking for contractor to perform installation works under Designs OLP02125, OLP02872. The Owner also plans to replace existing lighting fixtures (60 luminaires) and electrical wiring in Operations Subdivision No 2 (OS-2) Process Unit No 3 Air-Gas Compressor House (AGCH) (Lith. ODK) as part of the Occupation Risk Elimination and/or Mitigation Plan.

2.  Attachments.

2.1. OLP02125-272572-555 430-10-TDP-E for replacement of valves within tripping diagram - electrical part of design. 2.2. OLP02125-272572_553-430-10-TDP-PVA for replacement of valves within tripping diagram - PCA part of design. 2.3. OLP02872-V0 for replacement of existing inlet MoVs Esk-3-14, Esk-3-17, Esk-3-31 of compressors IK-301/1,2,R in Process Unit No 3 with new ROTORK valves. 2.4. OLP02872-272572_712-430-10-TDP-PVA_Rev._0_20260506 for replacement of existing inlet MoVs Esk-3-14, Esk-3-17, Esk-3-31 of compressors IK-301/1,2,R in Process Unit No 3 with new ROTORK valves. 2.5. KT-1/1 (TPP-63)EĮP ODK 3PS single-line diagram. 2.6. KT-1/1 (TPP-63)EĮP ODK 4PS single-line diagram. 2.7. List of Manufacturers.

3.  Description and specifics of work.

3.1.  General requirements.

3.1.1. To properly assess the situation and fully understand the scope of work, the potential Contractor must visit the site and familiarize themselves with the existing infrastructure prior to submitting proposal.
 All costs associated with such a visit and the preparation of proposal shall be borne by the potential Contractor.

3.1.2. Prior to submitting a proposal, potential Contractor must thoroughly review this Scope of Work and include in the proposal all works specified herein and attachments hereto. Any minor tasks not explicitly mentioned in this Scope of Work but required to ensure full functionality and completeness of works, shall be considered included in the proposal.

3.1.3. The Contractor shall provide all necessary equipment, labor, services, installation management, supervision, and all other resources required to execute the works in accordance with this Scope of Work. In the event of discrepancies between documents or if the technical information in the Scope of Work and/or its attachments is insufficiently detailed, the Contractor shall notify the Owner’s project manager or their authorized representative and follow their instructions.

3.1.4. All works shall be carried out in compliance with the effective laws, standards, and normative acts of the Republic of Lithuania, as well as with AB ORLEN Lietuva specifications and requirements.

3.1.5. The Contractor shall independently obtain all required permits/approvals for bringing their equipment and work tools into and out of the territory of AB ORLEN Lietuva in accordance with the procedures established by AB ORLEN Lietuva.

3.1.6. At the end of each shift, the Contractor shall tidy up the work site, sort and remove all waste generated during the execution of the works, and transport it using their own vehicles to the waste collection area within the Owner’s premises, in accordance with the Waste Management Regulations of AB ORLEN Lietuva.

3.1.7. All works shall be performed in accordance with AB ORLEN Lietuva occupational health and safety procedures available at:

https://www.orlenlietuva.lt/EN/ForBusiness/DocumentsForContractors/Pages/Occupational-Safety-and-Health-Documents.aspx

3.1.8. Where necessary, Contractor shall provide its staff with office and sanitary facilities and shall take care of the premises by keeping them clean and in good order.

3.2. Work description.

3.2.1. The Contractor shall perform all installation works required under process control and automation (PCA) part of the design.

3.2.2. The Contractor shall perform all installation works required under electrical part of the design in accordance with applicable legal regulations, normative documents and design solutions.

3.2.3. The Contractor undertakes to ensure the procurement and supply of all materials specified in the design, as well as minor materials not explicitly specified but necessary for the execution of the works, and such procurement shall be pre-agreed in writing with the Owner prior to ordering.

3.2.4. The Contractor shall perform all required electrical measurements, tests, and loop checks in accordance with Rules for Installation of Electrical Equipment, applicable legal requirements, and manufacturers’ specifications, and shall submit the corresponding measurement/test reports.

3.2.5. The Contractor shall carry out programming, parameterization, and commissioning of Rotork IQ electric actuators in accordance with the manufacturer’s technical requirements and design solutions.

3.2.6. The Contractor shall prepare and submit electric actuator setting/parameter configuration reports.

3.2.7. The Contractor shall prepare all design and as-built documentation, compile all required certificates and records, and prepare them for submission to the Owner’s archive.

3.2.8. The Contractor shall, at their own expense and without additional compensation, eliminate all defects and non-conformities identified during commissioning.

3.2.9. Installation works shall be carried out in stages within live power installation, with adjacent cubicles and/or equipment under voltage, without interrupting the technological process.

3.2.9.1. Stage I - commencement after signing the contract:

- install trays by 1 May 2027;

- install beakers, power and control cables by 1 May 2027;

- replace luminaires by 20 June 2027.

3.2.9.2. Stage II:

- MoV demounting/installation, connection and commissioning works - these works shall be performed exclusively during Refinery Turnaround 2027 (from 1 May 2027 to 20 May 2027).

3.2.10. The Contractor shall demount power and control cables (which will have to be replaced) from electrical panels to TPP-63 SVS-1,SVS-2, TPP-64 SVS, TPP-63 EIP ODK cabinets, panels as well as other equipment which will be no longer needed according to the design.

The Contractor shall replace existing lighting fixtures (60 luminaires) and electrical wiring in OS-2 Process Unit No 3 Air-Gas Compressor House (AGCH) (Lith. ODK) as part of the Occupation Risk Elimination and/or Mitigation Plan.

3.2.11. At OS-2 Air-Gas Compressor House (ODK), demount existing luminaires (60 pcs.), junction boxes and cables ~1000 m up to ODK 3PS (gr.12,14), ODK 4PS (gr.10,11) lighting cabinets.

3.2.12. At OS-2 Air-Gas Compressor House (ODK), install new luminaires (60 pcs.) with 1 ½ diameter stands and new junction boxes (80 pcs.).

3.2.13. Install new cable trays, AZ050 FT 50x50, ~300m.

3.2.14. Install luminaires at the elevation of 2.5 - 3.0 meters.

3.2.15. Install new cables (3x2.5) from ODK 3PS (gr.12,14) lighting cabinet to new luminaires, ~1000 m.

3.2.16. Replace power cable lines between boxes and replace cables to luminaires.

3.2.17. New luminaires must have numbering.

3.2.18. Prepare single-line diagrams in PDF and DWG formats.

3.2.19. Dismantled electrical and automation equipment that will no longer be used shall be delivered to the indicated area in the territory of the Owner.

The Contractor shall be responsible for the safety and organization of works in such conditions.

3.3.  Specific requirements.

3.3.1. During implementation of the project, the Contractor shall timely report the progress to the Owner. Procedure, scope and periodicity of reporting shall be defined in the contract and/or agreed in writing after contracting. 3.3.2. During installation and after its completion, the Contractor shall perform all mandatory inspections, measurements, and tests specified in the Electrical Equipment Testing Standards and Scopes, Rules for Installation of Electrical Equipment, and manufacturer documentation. All results must be recorded in the appropriate reports, and energization shall be carried out in accordance with AB ORLEN Lietuva applicable procedures. Energizing shall only be permitted in accordance with the procedures in force at AB ORLEN Lietuva and after obtaining all necessary approvals. 3.3.3. The Contractor shall perform the commissioning, adjustment, and testing of the installed equipment and systems, ensuring their readiness for integrated testing. 3.3.4. The Contractor shall prepare an energization schedule for the installed equipment, taking into account the project schedule and milestones, and shall coordinate it with the Owner. 3.3.5. The designer shall hold all permits and certificates required under LR legislation, authorizing the execution of design activities as specified in this design task (if applicable)..

  - . Qualification requirements for Contractor.

Provide proof of qualification or submit a written confirmation that the required documents will be presented before the conclusion of the contract:

3.4.1. Company registration certificate, or another document confirming registration in the Republic of Lithuania (copy);

3.4.2. Valid certificate issued by National Energy Regulatory Council of the Republic of Lithuania (Lith. VERT) for operation of energy facilities (electrical, thermal, liquefied petroleum gas, crude oil and petroleum products, natural gas), authorizing the performance of the works specified in the SoW, i.e., for certain types of works and activities;

3.4.3. Valid qualification certificates authorizing the Contractor to engage in the design and installation of control and automation systems for structures of exceptional significance;

3.4.4. List of subcontractors and their qualification documents (copies);

3.4.5. Proof of qualification issued for Contractor (subcontractor) by National Energy Regulatory Council of the Republic of Lithuania or Ministry of Environment (copies). Foreign companies shall provide, as part of the technical proposal, the documents valid in their country and equivalent to those indicated in Items 3.4.4 ÷ 3.4.8 (in English or translated into English language). Foreign companies must also provide confirmation that, prior to the signing of the contract, they will obtain and submit the relevant approvals from the National Energy Regulatory Council of the Republic of Lithuania or the Ministry of Environment, confirming that their qualification documents are valid in the Republic of Lithuania. Absence of such confirmation shall result in disqualification of potential Contractor.

3.4.6. Documents granting the right to operate electrical equipment (operation of electrical networks and equipment up to 1000 V; testing of electrical networks and equipment up to 1000 V);

3.4.7. Documents authorizing the performance of works within the scope of this design (electrical equipment up to 1000 V, process control and automation systems, electronic communications/telecommunications, and other related fields);

3.4.8. The works will be carried out on live electrical installations; therefore, the Contractor’s and subcontractor’s personnel must be authorized to work on such installations in accordance with the applicable normative documents of the Republic of Lithuania. Employees must hold valid energy worker qualification certificates granting the right to perform electrical works on live electrical installations up to 1000 V (operation of electrical networks and equipment up to 1000 V, testing of electrical networks and equipment up to 1000 V, relay protection and automation for electrical networks up to 1000 V).

3.4.9. Provide a list of works of similar scope and technical parameters completed by the Contractor over the past 3 years. The list shall include: the name of the company where the works were performed; description of the works; year of execution; value of the works; and contact persons. Attach any other documents supporting the Contractor’s experience;

3.4.10. The Contractor shall have sufficient qualified personnel to perform the works specified in this Scope of Work.

3.4.11. The Contractor shall have experience in programming, parameterization, and commissioning of Rotork IQ electric actuators. Attach any other documents supporting the Contractor’s experience;

3.4.12. Provide a list indicating where and when commissioning and setup works of Rotork actuators have been performed.

  - . Requirements for technical proposals.

3.5.1. Specify the types and technical data of proposed equipment.

3.5.2. Provide a detailed work execution schedule created using MS Project or similar scheduling software. The schedule shall include the supply of materials and the execution of installation works.

3.5.3. Indicate delivery terms for the materials.

3.5.4. Submit detailed estimates. Provide estimated work hours.

3.5.5. Do not include ESK 3-36-1, ESK 3-36-R, ESK 2-16-1, ESK 2-16-2 into your proposal as these MoVs have been already installed.

3.6.  Requirements for documentation.

3.6.1. Technical documentation shall be prepared and submitted to the Owner in accordance with the applicable normative documents of the Republic of Lithuania and the specific requirements of the Owner.

3.6.2. Product and material passports, certificates, and declarations of conformity shall be submitted to the Owner in their original language.

Design documentation (DD) – drawings, diagrams, specifications, logbooks, etc. shall be presented to the Owner for review and comments in a digital form (PDF, DWG format).

For final approval of DD, the Contractor shall submit a hard (original) copy of DD signed by both the designer and design part manager, also an electronic copy of DD (PDF and DWG format, texts in MS Word DOC format, MS Excel XLS format, if any). Original copy of DD shall have OL approval mark ‘APPROVED FOR CONSTRUCTION’ or ‘APPROVED’.

3.6.3. As-built documentation packages shall be compiled in separate folders, with each document provided as an individual file. The file name shall be formed using the document reference number from the register and the document title or number.

4.  Materials, equipment, and services to be provided by the Owner.

4.1. DCS programming works; 4.2. Scaffolding; 4.3. Organization/coordination of equipment disconnection; 4.4. Organization of MoV demounting/installation; 4.5. Materials provided by the Owner: 4.5.1. List of materials under OLP02125 electrical part:

|  | Name and technical characteristics of materials under OLP02125 | Qty |
| --- | --- | --- |
| 1.1 | 450/700 V cable with solid copper conductors, PVC conductor insulation, PVC sheath insulation, armored (steel tape), suitable for surface installation, UV-resistant, flame retardant in accordance with IEC 60332-1. 4 cores, conductor cross-section 2.5 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø15 mm, cable color: black. | 1750 m |
| 1.2 | 450/700 V cable with solid copper conductors, PVC conductor insulation, PVC sheath insulation, armored (steel tape), suitable for surface installation, UV-resistant, flame retardant in accordance with IEC 60332-1. 4 cores, conductor cross-section 4 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø16 mm, cable color: black. | 585 m |
| 1.3 | 450/700 V cable with solid copper conductors, PVC conductor insulation, PVC sheath insulation, armored (steel tape), suitable for surface installation, UV-resistant, flame retardant in accordance with IEC 60332-1. 4 cores, conductor cross-section 6 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø18 mm, cable color: black. | 760 m |
| 1.4 | 450/750 V flexible cable for flexible installations, with PVC sheath insulation, suitable for surface installation, UV-resistant, flame retardant. 4 cores, conductor cross-section 2.5 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø13.5 mm, cable color: black. | 45 m |
| 1.5 | 450/750 V flexible cable for flexible installations, with PVC sheath insulation, suitable for surface installation, UV-resistant, flame retardant. 4 cores, conductor cross-section 4 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø15 mm, cable color: black. | 15 m |
| 1.6 | 450/750 V flexible cable for flexible installations, with PVC sheath insulation, suitable for surface installation, UV-resistant, flame retardant. 4 cores, conductor cross-section 6 mm². Operating temperature: -40°C to +70°C, outer cable diameter Ø16.5 mm, cable color: black. | 15 m |
| 2.1 | 6420680 AW 15 21 FT. Wall-mounted and support bracket with welded plate, B210mm St FT | 56 pcs. |
| 2.2 | Galvanized steel pipe DN ¾, standard EN 10255-M, dimensions 26.9 × 2.6 mm, length 5.8–6 m. | 28 pcs. |
| 2.3 | Hot-dip galvanized U-bolt 3/4"; thread M8; diameter D1 – 26.9 mm; length L – 63 mm; width k – 35 mm; manufacturer: CORTEM. | 56 pcs. |
| 2.4 | Perforated angle bracket, hot-dip galvanized, steel thickness 3 mm; length – 3 m sections; type KTT 50×50/3-F, perforated angle 3.0 mm, standard (STD) | 10 pcs. |
| 2.5 | End-of-pipe edge protection with earthing element, type DBT2A, thread 3/4" F (ISO 228); manufacturer: CORTEM | 56 pcs. |
| 2.7 | Protective conduit, flame-retardant, inner diameter Ø22.8 mm, outer diameter Ø28.5 mm, M/PG 32/21, black polyamide, class 6 resistance (400 N / 100 mm), temperature range from -40°C to +150°C, type PA‑REB‑23F | 20 m |
| 2.8-2.10 | Malux circuit breaker, 3P, 20 A, 2G Ex de IIC T6, code GHG2622301R0002 | 8 pcs. |
| 2.11-2.13 | Explosion-proof power switch, Ex II 2G, EEx ed IIC T6, IP66, 3P, rated voltage Un – 400 V AC, rated current In – 10 A, catalogue No. GHG 261 0005 R0009, Malux | 4 pcs. |
| 2.17 | Circuit breaker GV2ME21 17..23A,3P | 1 pcs. |
| 2.18 | Automatic circuit breaker + reversing contactor with mechanical interlock (GV2ME20 + | 5 pcs. |
| 2.19 | Circuit breaker GV2ME16+ | 1 pcs. |
| 2.20 | Automatic circuit breaker GV2ME10, 4–6.3 A, 3P, with magnetic trip at 78 A, breaking capacity Icu 1 | 2 pcs. |
| 2.21 | Circuit breaker GV2ME05 | 6 pcs. |
| 2.24 | Metal blind M40x1.5 –60 °C to +200 °C, Ex d II Gb / Ex d IIC, IP6 | 14 pcs. |
| 2.25 | Metal blind M25x1.5 –60 °C to +200 °C, Ex d II Gb / Ex d IIC, IP66 | 28 pcs. |

4.5.2. List of materials under OLP02125 PCA part:

|  |  | Qty |
| --- | --- | --- |
|  | MoV with Rotork IQ actuator | 13 pcs. |
| 1. | Junction box Ex ll 2G Ex ed IIC T6 Gb IP66 according to attached Specification 02125-JB-01-D | set |
| 2. | Junction box Ex ll 2G Ex ed IIC T6 Gb IP66 according to attaches Specification 02125-JB-02-D | set |
| SP-XSF-Esk-3-22 | Overvoltage protection VSSC4 SL FG24VAC/DCO.5A, Weidmuller | 1 pcs. |
| K* | Auxiliary relay PLC-BSC- 24DC/21-21 ( 2967015) + REL-MR- 24DC/21-21,2 CO contact, 24VDC (2961192) Phoenix Contact | 42 sets |
| 1. | Cable ÖLFLEX® CLASSIC 110 CY BK 12G1.5 black (0.6/1kV) | 2240 m |
| 2. | Cable YSLYCY-JZ 600 18x1.5, 0.6/1 KV BK | 400 m |
| 3. | Cable RE-2Y(St)Yv PiMF 2x2x1.3 black, cat. No. 20133, Helukabel | 1320 m |
| 6.17 | Cable tray edge protection strip KSB 2, PVC (0.75–2 mm), Art. No.: 6072909 | 5 m |
| 6.1 | Duct 50x50mm, AZK 050 FT, 6075142 "OBO BETTERMANN" | 162 m |
| 6.2 | Tray cover AZDU 50 DD "OBO Bettermann", code 6080158 | 162 m |
| 6.3 | Connector for AZ cable tray VF AZ FT, 100 × 46 mm, Art. No.: 6066550, OBO Bettermann (including 4 fastening bolts) | 108 pcs. |
| 6.8 | Strip clamp SBV 15 A2, single-sided, 20 × 18 mm, stainless steel V2A (A2, 2B), code 6490964, OBO Bettermann | 276 pcs. |
| 6.9 | Perforated cable tray SKS120FT, 200 × 110 × 1.5 × 3000 mm, hot-dip galvanized, catalogue No. 6061621, OBO Bettermann | 180 m |
| 6.10 | RLVL110FT longitudinal connector, catalogue No. 6067913, OBO Bettermann | 208 pcs. |
| 6.11 | Cover DRLU/200 DD, hot-dip galvanized, catalogue No. 6052650, OBO Bettermann | 180 m |
| 6.12 | Cover holder DKU, catalogue No. 6065600, OBO Bettermann | 40 pcs. |
| 6.14 | Bolt with nut 12510/M6×12, hot-dip galvanized, catalogue No. 6406122, OBO Bettermann | 322 pcs. |
| 6.15 | Cable tray SKS110FT, hot-dip galvanized, 100 × 110 × 1.5 × 3000 mm, hot-dip galvanized, catalogue No. 6061605, OBO Bettermann | 130 m |
| 6.16 | Channel cover 100 mm, without fast., length 3 m, DRLU 100 DD, code 6052643, OBO Bettermann | 130 m |
| 6.18 | Cable support 20F/1000, 718249, WIBE | 30 pcs. |
| 6.5 | Partition connector TSGV A2 V2A 1.4310 2B, OBO Betterman, cat. No. 6067970 | 112 pcs. |
| 6.7 | Mounting strip SBR 15 A2K, code 6490282, RAL 9005, OBO Bettermann (1 pack = 25 m). | 122 m |
| 6.6 | Partition clamp KS KR A2 for cable tray, V2A, catalogue No. 6062280, OBO Bettermann | 226 pcs. |
| 6.13 | Partition TSG 110 DD for cable trays, 110 × 3000 mm, steel, hot-dip galvanized (DD), OBO Bettermann, catalogue No. 6062335 | 310 m |
| 6.20 | Anchor BZ-U 8-30-41/95 M8x95mm St G 3498326 OBO Betterman | 120 pcs. |
| 7. | Z-shaped perforated angle bracket ZC30H35/3-F, steel thickness 2 mm, length – 3 m sections, BAKS 06304303 | 15 m |
| 6.4 | Partition for cable trays and ladders, 45 × 3000 mm, steel, hot-dip galvanized (DD), type TSG 45 DD, catalogue No. 6062321 | 27 m |

4.5.3. List of materials for replacement of existing lighting fixtures (60 luminaires) and electrical wiring in OS-2 Process Unit No 3 Air-Gas Compressor House as part of the Occupation Risk Elimination and/or Mitigation Plan:

|  |  | Qty |
| --- | --- | --- |
| 1. | LED luminaire LELED3NBUSND, Appleton, ambient temperature (Ta) -40°C to +65°C, IP66, IK10, 4000 K, length 0.7 m, 26 W, ATEX/IECEx certified | 60 pcs. |
| 2. | Cable CYKY 3x2.5 | 1000 m |
| 3. | Cable tray AZ050 FT 50x50 | 300 m |
| 4. | Tray cover AZDU 50 DD "OBO Bettermann", code 6080158 | 300 m |
| 5. | Galvanized steel pipe 1 1/2" (DN40) x3.2mm | 200 m |
| 6. | Shelf WW200 | 200 pcs. |
| 7. | Ex junction box with terminals GHG7910101R0002 (GHG7910102R0345) for Zone 1/21, 4x21 cable glands, casted polyamide, IP66, T: -55...+40°C, marking: II 2 G Ex dem ia II, IIC T6 II 2 D Ex tD A21 | 80 pcs. |

4.5.4. List of materials under OLP02872 electrical part:

|  | Name and technical characteristics of materials under OLP02872 | Qty |
| --- | --- | --- |
| 2.2 | Malux circuit breaker, 3P, 20 A, 2G Ex de IIC T6, code GHG2622301R0002 | 3 pcs. |
| 1.2 | Cable H07RN-F 4×6 (rubber-sheathed, flexible) | 100 m |
| 1.1 | Cable JZ-600 Y-CY (YSLYCY) 4×6, black, shielded, 11599 | 200 m |
| 2.5;2.12 | Seal M25x1.5, EEx d IIC/ EEx e II, 25 A2FRC1RA, "CMP" | 6 pcs. |
| 2.8 | Seal M32x1.5 EEx d IIC/EEx e II, 32A2FRC. "CMP" | 3 pcs. |
| 2.10 | Galvanized steel Z-profile ZC25H 25/2 | 10 pcs. |
| 2.2 | Motor circuit breaker GV2ME16, 9–14 A, 3P, with magnetic trip, Schneider Electric | 2 pcs. |

4.5.5. Materials under OLP02872 PCA part shall not be provided by the Owner.

5. Materials and equipment to be provided by the Contractor:

| 5.1. All other materials not specified in Section 4, but required for the execution of the works under the design, shall be supplied by the Contractor. 5.2. The Contractor shall agree with the Client on the type, model, manufacturer, and key technical parameters of the supplied materials and equipment, in accordance with the List of Manufacturers approved by the Owner (see Manufacturers List rev.7 (2026_02)). 5.3. Materials shall be supplied together with technical documentation in accordance with the requirements of the legal acts of the Republic of Lithuania and the Owner, including CE marking, declarations of conformity or certificates confirming that the products are certified in Lithuania, declarations, certificates, manufacturer test reports, and operation, use, and operational control manuals in the Lithuanian language, etc. 5.4. The Contractor shall provide all materials, equipment, machinery, personal protective equipment, and special safety measures (where required) necessary for the execution of the works specified in the Scope of Work. 5.5. All equipment used by the Contractor shall be certified, metrologically verified (where applicable), and comply with the occupational health and safety requirements of the European Union. |
| --- |
| 6. Requirements for work completion. |  |
| 6.1. In accordance with the procedure established by the Owner, the Contractor shall prepare and submit to the Owner handover technical documentation, and eliminate any identified defects and non-conformities. The Client shall issue the relevant certificate confirming that the electrical installations are fit for use. 6.2. The Contractor shall complete all construction and installation works, measurements and tests, commissioning and start-up activities, and shall issue mechanical completion acceptance statement. |  |

7. Requirements for work schedule.

7.1. Provide estimated work hours in the proposal.

7.2. With proposal, present detailed equipment and materials procurement, delivery and work execution schedule with clear indication of all dated milestones, including equipment delivery, installation, commissioning, performance test, handover for operation and submission of technical documentation.

7.3. Start of installation work (after signing the contract) - 1 October 2026.

7.4. Commissioning, performance test, handover/validation for operation and submission of technical documentation (obtainment of certificate of acceptance of installed equipment as fit for use from technical supervision area of the Owner) - by 19 May 2027.
7.5. Other minor works (site cleaning, covering of trays and other minor tasks that do not limit the startup) - by 30 June 2027.

7.6. Payments are estimated from 30 January 2027.

Description; Value; Qty. Electrical and automation installation works; Man-hours; +. Labour (for diagnostics), EUR; -. Materials, EUR; +. Equipment, EUR; +. Total, EUR:; +.

# Prepared by:

# Vitalij Tarasov

# Engineer Expert

# Maintenance Subdivision